## Slide 1: Breaker Failure Schemes
Breaker Failure tutorial
PES GM
July 2010

## Slide 2: Schemes
Topology dictates scheme
  Single Phase Tripping
  Minimal Current
  Critical Clearing Time
  Multifunction relay
Type of Breaker
  Gas
  Vacuum

## Slide 3: Breaker Failure Schemes
Simple Basic
ReTrip
Elimination of 50BF Reset Time
Control Timer
Dual Timer
2 step timing
Breaker Failure Seal in

## Slide 4: Breaker Failure Schemes
Triple Timer
Single Phase with Re trip
Breaker Failure with Bypass
Multiple Scheme Breaker Failure

## Slide 5: Basic Breaker Failure Scheme

## Slide 6: 50 BF – Current Detector
Phase
  Set to detect most sensitive fault
  Possible above load current
    No danger of operation during trip testing
  If Opening resistors
    Allow for condition resistor inserted but main contacts fail

## Slide 7: 50 BF Current Detector
Ground Overcurrent
  Detect all ground faults
  Set high enough so not delayed by dc current decay in ct circuit following a breaker operation and ct saturation

## Slide 8: Delayed dropout
Elements that operate on ac and dc magnitudes
Elements that operate on dI/dt if it detects di/dt of decaying dc.

## Slide 9: Timing Chart

## Slide 10: Breaker Failure Timer
Set greater than the Breaker interrupt time plus drop out of 50BF current Detector
Margin accounts for maximum operate times
Total fault clearing is less than transient stability time

## Slide 11: Total Clearing Time
Less than transient Stability Time – 10 – 30 cycles ( 4 cycles !)
Less than time for damage to major equipment may occur – greater than 30 cycles
Less than time damage to industrial processes may occur – greater than 30 cycles

## Slide 12: Critical Clearing Time for Stability Factors
Severity of Fault
Loading on system
Mass of Generators
Type of fault

## Slide 13: Faults
More severe must be removed faster
Three phase faults must be removed faster than single line to ground faults

## Slide 14: Time Coordination
No need to coordinate with external zones of protection
BF Scheme must provide lockout to prevent reclosing

## Slide 15: Retrip
Give the breaker one last chance to clear the fault before the BF scheme operates
May use separate trip coil on breaker
May or may not have time delay
Should alarm maintenance knows tripped on retrip.

## Slide 16: Breaker Failure Re-Trip

## Slide 17: Elimination of 50 Reset
Slow reset time for electromechanical relays
Due to dc offset some microprocessor relays may slow reset
Timer times out before look for 50BF pickup

## Slide 18: Elimination of 50BF Reset Time

## Slide 19: Fault Clearing Timing Chart

## Slide 20: Control Timer
Limits how long you wait for 50BF before scheme resets
Coordinate with Synch Check reclosing time delay

## Slide 21: Addition of Control timer

## Slide 22: Two Step Timer
Need to clear three phase faults faster than other faults
Distinguish between single phase and multi phase faults
Set timer for single phase faults slower than timer for multi phase faults

## Slide 23: Two Step Timer

## Slide 24: Seal In
Some Breaker Failure Initiate contacts don’t stay maintained
Use output for seal in input as long as current detector remains picked up.

## Slide 25: Breaker Failure Seal-In

## Slide 26: Minimum Current Scheme
Used where current is too low for current detector operation.
  Transformers
  Reactors
  Generators
  Filter Banks

## Slide 27: Minimal Fault Current

## Slide 28: Dual Timer with 52aa and 50BF Reset

## Slide 29: Triple Timer

## Slide 30: Single Phase Retrip

## Slide 31: Breaker Failure Timer Bypass

## Slide 32: Multiple Scheme within Relay

## Slide 33: Questions ?