## Slide 1: Breaker Failure Tutorial PES General Meeting July 2010

## Slide 2: Breaker Failure Protection
Definitions (Guide 3.0)
Need for BF Protection (Guide 4.0)
Backup Protection (Guide 5.0)
  Considerations
  BF Protection
Breaker Failure Modes (Guide 6.0)
  Failure to Trip
  Failure to Clear
  Incorrect Breaker Operation

## Slide 3: Definitions

## Slide 4: Primary Protection
The main protection system for a given zone of protection that operates in the fastest time and removes the least amount of equipment from service.

## Slide 5
1
2
G
21
21
Overreaching Pilot Trip
Overreaching Pilot Trip
G
Reverse Block
Overreaching
Reverse Block
Overreaching
Transceiver
Transceiver
Overreaching Line Protection

## Slide 6: Backup Protection
A protection scheme for the same zone of protection as the primary protection but may be slower and removes the same or additional equipment from service. Backup protection may be installed locally, i.e. in the same substation as the primary protection, or remotely.

## Slide 7: Breaker Failure Protection
This protection is specifically relied upon to take appropriate action to clear a fault when the breaker that is normally expected to clear the fault fails to do so for any reason.

## Slide 8: Local Breaker Failure Protection
A backup protection system that is in the same substation as the primary protection.

## Slide 9
SW
SW
B3
SX
SY
SZ
F1
F2
F3
DB
D1
D2
D3
M
B1
SZ
SX
SY
Line BX
Line BW
B
SUBSTATION
F
SUBSTATION
Line FY
Line
FB
Line FZ
B2
Fault on BX, B3 Opens, B1 Fails
Fault on FB, F1 Fails
Notes: For example consider the networked system shown above.
For the failure of F3, all adjacent circuits need to be tripped
Using remote BU, relays at Bell, Y and Z must detect the uncleared fault and trip.
Using local BU, directly trip F1 and F2
SZ would trip by remote BU or TT

## Slide 10: Local BF Protection Possible Disadvantage
May use some of the same equipment, such as transducers, batteries, and circuit breakers as the primary protection and can, therefore, fail to operate for the same reasons as the primary protection.

## Slide 11: Remote Backup Protection
Historically, the first set of backup protection that was installed. It is completely independent of the relays, transducers, batteries, and circuit breakers of the primary protection system it is backing up by virtue of its physical location.

## Slide 12: Remote Backup Protection-Advantage
No common mode failures that can affect both protection systems.

## Slide 13
G
21
21
2nd Zone Backup Trip 120%
2nd Zone Backup Trip 120%
G
Step Zone Backup Protection
First Zone Backup Trip 90% of Line
First Zone Backup Trip 90% of Line
3nd Zone Backup Trip 150 to 200%
3nd Zone Backup Trip 150 to 200%

## Slide 14: Remote Backup Protection-Disadvantages
Remote protection may remove more system elements than is desirable or necessary to clear a fault.
As the power system matured, it became increasingly difficult for remote protection to detect (see) all the faults that the primary protection could detect.

## Slide 15
SW
SW
B3
SX
SY
SZ
F1
F2
F3
DB
D1
D2
D3
M
B1
SZ
SX
SY
Line BX
Line BW
B
SUBSTATION
F
SUBSTATION
Line FY
Line
FB
Line FZ
B2
Fault on BX, B3 Opens, B1 Fails
Notes: For example consider the networked system shown above.
For the failure of F3, all adjacent circuits need to be tripped
Using remote BU, relays at Bell, Y and Z must detect the uncleared fault and trip.
Using local BU, directly trip F1 and F2
SZ would trip by remote BU or TT

## Slide 16: Control Timer
A timer that limits the amount of time the breaker failure scheme is active after initiation.

## Slide 17: Addition of Control timer

## Slide 18: Critical Clearing Time
the longest time that fault conditions may persist before system stability is lost.

## Slide 19: Critical Clearing Time Establishes Max Duration of the Timing Chart

## Slide 20: Definitions
Definitions are only intended to facilitate communication.
Not rigidly applied as with a spec
Definitions applied to individual elements may vary with application, i.e. Primary and Backup (OC and 2nd Zone)
Notes: Outline of material to be covered in this talk.

## Slide 21: The Need for BF Protection

## Slide 22: The Two Laws Relay Engineers Live by:
MURPHY’S LAW
  If it can go wrong, it will go wrong
Ohm’s Law
Notes: Outline of material to be covered in this talk.

## Slide 25: While Infrequent, Circuit Breakers:
Fail to trip
Fail to clear
And other circuit breakers must isolate the sources
Without BF, results can be devastating
Notes: Outline of material to be covered in this talk.

## Slide 26: Why Breaker Failure Protection ?
A
B
C
LOAD
LOAD
LOAD
FAULT
8
6
4
3
5
7
2
1

## Slide 27: Need for BF Protection (cont)
As per definitions, there are two types of backup protection:
  Remote
  Local
Breaker Failure is considered a subset of backup protection
Notes: Outline of material to be covered in this talk.

## Slide 28: Remote BF Backup Protection
Disadvantages:
  All adjacent lines must be overreaching
  Remote BU scheme doesn’t know when the local breaker is commanded to open; has to allow time for slowest time delay line trip plus margin
  Tapped loads are dropped, causing wide spread customer outages

## Slide 29: Remote BF Backup Protection (cont)
  Lengthy backup TD causes excessive volt dip duration, additional fault damage, possible damage to unfaulted equipment, instability
  Infeed effects makes it difficult to see the entire length of adjacent lines
  To get reach, line may trip on heavy load
Advantage:
  Completely independent of PR’s, control systems and battery at station of failed breaker

## Slide 30: Remote BF Backup
A
B
C
LOAD
LOAD
LOAD
FAULT
8
6
4
3
5
7
2
1

## Slide 31: Local BF Backup Protection
Advantages:
  Eliminates disadvantages of remote backup
  Local BF gets trip signal from local line PR
  Local BF protection starts a timer
  If time expires, trips local breakers (in example)
  In most cases, tapped loads are unaffected
  Total clearing time reduced substantially
  Timer setting <12 cycles vs. 30 for remote

## Slide 32: Local BF Backup Protection (cont)
  Could mean the difference between a stable and unstable system for critical faults
  Reduce the extent of fault damage by reducing time fault is on the system
Disadvantage: Common Mode Failure
  Station battery, failure of initiating relay
  Greatly improved with numeric multifunction technology

## Slide 33: Local BF Backup
A
B
C
LOAD
LOAD
LOAD
FAULT
8
6
4
3
5
7
2
1

## Slide 34: Backup Protection
At electric utilities, many aspects of protection philosophy are experience-based.
As we found in putting this guide together, each utility thinks their way is the right way and in some cases, the only way.
Finding common ground for consensus building is what the IEEE/PSRC does best.

## Slide 35: Backup Protection Considerations (cont)
Properties of Ideal local backup:
  Should be completely independent of the primary protection scheme
  Should have physically and electrically independent relays, CTs, PTs CBs with redundant battery systems
  And… we all know it’s cost prohibitive.

## Slide 36: Backup Protection Considerations (cont)
A reasonable level of local BU protection can be accomplished with:
  Duplicated tripping systems (primary 1 and 2)
  That are independent and galvanically isolated
  Operate in a 1-out-of-2 tripping arrangement
  Each tripping system initiating BF
  BF tripping adjacent breakers to clear the fault

## Slide 37: Backup Protection Considerations (cont)
Where local BF is required, Protection system failure should not be a cause of breaker failure.
Redundant relaying systems as independent as practical should be used.
Each system may operate a separate or both breaker trip coils, directly or indirectly

## Slide 38: Methods Used to Provide Breaker Failure Protection
Timer initiation from a trip relay contact
Monitoring reset of the trip relay contact
Monitoring reset of OC fault detector
Monitoring reset of CB aux contact
  Relying on aux contacts may prove unreliable
  CB main may open but fail to interrupt
  Linkage fails, welded contact, no aux operation
  Low or no current situations require use of aux

## Slide 39: Breaker Failure Protection
BF function can be implemented using:
  Separate hardware
  Integrated in primary and BU protection hardware
BF required for single and 3-phase tripping
BF time delay:
  Long enough for successful fault clearing plus margin
  Proper Margin prevents needless operations

## Slide 40: Breaker Failure Protection (cont)
Some schemes reset when BFI resets
Some seal the initiate and reset when current goes away
Some are combinations of both

## Slide 41: Breaker Failure Protection (cont)
BF may initiate a re-trip signal to the CB:
  Prior to BF output with margin (last chance trip)
  3-phase tripping or individual poles for selective single phase tripping
  If BF is integrated in same hardware, use different output contact for re-trip from initial trip output

## Slide 42: Breaker Failure Protection (cont)
Low current or no current applications, use aux contacts
  Weak or zero in-feed, voltage trips, etc
  current supervision is most secure and reliable

## Slide 43: Breaker Failure Modes
BF should operate when:
  A breaker is “told” to trip by PR’s but does not successfully interrupt a fault
BF is considered a subset of local BU protection
BF is also referred to as “Stuck Breaker”

## Slide 44: Breaker Failure Modes
Failure to Trip
Failure to Clear

## Slide 45: Failure to Trip:
Trip circuit energized by PR scheme
Main breaker contacts do not open
  Open or short in trip circuit wiring
  Open or shorted trip coil
  Mechanical problem

## Slide 46: Failure to Clear:
Main Contacts Open
Arc not extinguished, current continues to flow through main contact
  Mechanical problems (incomplete opening)
  Loss of dielectric (dirty oil, vacuum, gas)

## Slide 47: Failure to Clear (cont):
Aux contacts change state, not a reliable indicator of successful breaker opening
Opening resistors inserted, main contacts fail to open, high Z current flow

## Slide 48: Incorrect Breaker Operation, Not Classified as BF:
Non-fault “Lock on” for loss of dielectric
Contact Flashover
  Restrike of an opening breaker
  Surge through an open breaker contact
Failure of a Breaker to close
Non-fault related failures during switching
  Failure to interrupt load
  Mechanical failure

## Slide 49: Impending Failures Identified with Numeric Relays:
Identifying degraded performance:
  Changes in operate or clearing time
  Accumulated interrupted current
  Number of operations

## Slide 50: Breakers with Single-Phase Tripping:
Present additional constraints for BF protection

## Slide 51: Questions ?