## Slide 1: BF Communications Standard Section 10
Breaker Failure Tutorial
PES GM
July 2010

## Slide 2: Tripping Remote Line Breaker
Grounding switches (pyrotechnic, SOGS) – an ugly old solution for remote tripping, in widespread use.
  Slow – 20 added cycles clearing delay
  Applies another fault to the system – can’t help!
  How to block reclosing?
Stop blocking carrier – remote end trips, but will it reclose?
Use Direct Transfer Trip (DTT) channel to trip the remote breaker for a BF after an adjacent-zone fault – fast and effective, expensive.
New carrier sets and voiceband data sets (tone replacements) for line pilot protection have DTT capability added.
Dedicated fiber pilot channels have DTT capability.

## Slide 3: BF After DTT from Remote End
If DTT is received for primary protection (line protection, line reactor isolation, remote transformer, etc.), initiate BF.
If DTT is received for a remote BF backup trip, do not initiate BF (no cascaded BF protection).
If DTT initiates BF, be ever so careful about testing or working on channel equipment!
Option for remote sites – allow reclosing when DTT channel resets, for easy restoration.

## Slide 4: DTT Security
Use FSK carrier, FSK tones, or continuous data transmission to constantly monitor channel integrity (it is almost never used).
For high security, dual FSK channels have been used with tripping frequency shifts in opposite directions (frequency translation protection).
Data sets can be expected to be much more secure.
Overcurrent or directional overcurrent supervision of DTT improves security.

## Slide 5: Unified protection, control, and automation LAN
100 Mbit/s
Ethernet Switch
Process Bus
Router
to EMS WAN
Local Operator Interface Computer
Substation Data Base Server
Relay
Relay
IED
Relay
Relay
IED
Relay
Relay
IED
Station LAN
Process Bus
Line Zone Intelligent Power Apparatus
Bus Zone Intelligent Power Apparatus
Transformer Zone Intelligent Power Apparatus
100 Mbit/s
Ethernet Switch
100 Mbit/s
Ethernet Switches

## Slide 6: Use High Speed LAN for BF
Optical Ethernet local area network (LAN) with IEC 61850 GOOSE messaging replaces masses of dedicated wiring.
Use to send BFI from one zone relay to other BF relays, or zone relays with embedded BF functions, over the shared LAN.
Use to send BF Trips from BF relay to breaker control relays over shared LAN.
Use to send lockout (block close; cancel reclosing) commands to breaker control relays.

## Slide 7: UCA®/IEC 61850 GOOSE (or GSSE) Messaging for LAN Control
Generic Object Oriented Substation Event.
A relay or IED can send a sequence of control or status point messages to replace control signals on a dedicated wire.
Not just a single message to request remote action…
A process to continuously send intended state from transmitting IED – like a contact that picks up and drops out at critical moments.
Even if the receiving IED was turned off when the first trip message was sent and is turned on later, it will be able to get a later update on the status it missed.

## Slide 8: UCA®/IEC 61850 GOOSE (or GSSE) Messaging for LAN Control
GOOSE message comprises an array of status bits.
Each source-identified array is sent periodically over the LAN, at a user-set rate.
Also send GOOSE instantly if any bit changes state.
Reliability through repeated, unacknowledged messages.
A sending IED can “publish” the identity of available status bits, that can contain control commands.
Any other IED can “subscribe” to this message – many connections can be established with multicast efficiency.
Many new settings to define what used to be wired connections.
“SMART GOOSE” proposed to preconfigure some of the connections that would normally be needed when IEDs are commissioned.

## Slide 9: BFI via GOOSE Messaging

## Slide 10: BF Tripping via GOOSE messaging

## Slide 11: UCA®/IEC 61850 GOOSE (or GSSE) Messaging for LAN Control
Speed consistency could be impacted by Ethernet collisions and retries at a busy time.
This can be minimized by use of switches rather than hubs.
IEDs prioritize and filter their message transmissions.
New & valuable – if periodic GOOSE update is not received by every subscribing IED, each can alarm the failure.
Self monitoring process can eliminate most maintenance testing. Wires cannot do this!
At last – safe and continuous monitoring of the whole BF scheme including the tripping chain.