## Slide 1: Breaker Failure Relay Testing
Breaker Failure tutorial
PES General Meeting
July 2010

## Slide 2: Testing
Due to the importance of these schemes and the possible catastrophic consequences should the scheme fail to operate, initial and periodic testing is recommended.
However, users must be very careful when testing these schemes.

## Slide 3: Consequences of Erroneous Breaker Failure (BF) Tripping
Dropping local loads,
Interrupting multiple transmission paths,
Tripping remote breakers with the possibility of dropping tap loads,
And tripping or causing instability in generators.

## Slide 4: GENERAL GUIDELINES Following are general guidelines to be considered when testing BF schemes

## Slide 5
Contact with the manufacturer should be maintained to keep abreast of bulletins issued covering possible component or firmware changes necessary

## Slide 6
A thorough review of drawings is necessary to determine all possible BF initiation (BFI) sources and trip paths. For example, some schemes trip the bus differential auxiliary relay.

## Slide 7
Clause 8 addresses isolation switches to allow maintenance and testing of the scheme are required. This is especially true if the breaker failure functions are part of existing primary protection. Separate BF outputs should be wired through isolation switches to facilitate isolation for testing.

## Slide 8
Clause 8 also addresses the use of auxiliary tripping relays. Although auxiliary tripping relays have their disadvantages (additional failure point, additional time delay), it is more difficult to test the BF scheme without them and could necessitate a complete station outage in order to perform adequate tests.

## Slide 9
While it is possible to test a BF relay with its corresponding breaker in service, it is generally advisable to isolate the breaker to reduce the possibility of an erroneous trip output (i.e., test the BF relay when the breaker is out for scheduled maintenance). Testing the BF relay with the breaker in service can be especially risky if the phase current detectors are set below expected load.

## Slide 10
BF trip outputs should be isolated whenever test current is passed through the BF relay current coils and/or whenever the relays that provide a BFI signal are being trip tested.

## Slide 11: BENCH-TESTS A full set of commissioning bench-tests is recommended prior to placing a new BF relay in service

## Slide 12
Perform initial testing as per the manufacturer's recommended initial test procedure as found in instruction manuals and/or application guides. This should include testing phase and ground current detectors, breaker failure (and any other) timers, and inputs (breaker failure initiate, low SF6 gas pressure indication, pallet interlocks, etc).

## Slide 13
Apply relay settings according to the specified settings provided by the protection engineer, and test current detectors and timers according to the desired settings.

## Slide 14
On electromechanical models, mechanical inspection – for broken/damaged components, tight connections, contact gaps/wipe as applicable

## Slide 15: IN-PANEL TESTS With the relay installed in the current/tripping circuits, the following tests should be performed (with trip outputs isolated or limited)

## Slide 16
Passing test current from the breaker CT to the relay and reading it in the relay (with external ammeter and/or with relay display)

## Slide 17
Test trip paths designed to provide a BFI input
Test loss-of-dielectric conditions by simulating low SF6 or air pressure (if applicable)

## Slide 18
Test the BF scheme as a system, simulating a fault condition with primary relays in series with BF relay; block tripping by primary relays and allow the BF relay to provide re-trip for the breaker as applicable, then allow the BF relay to trip the auxiliary relay

## Slide 19
On commissioning, allow the BF trip auxiliary relay to trip the breakers, send transfer-trip, etc, as designed
Test the 52a contact input to the BF scheme by operating the protected breaker and monitoring the auxiliary contact's status.

## Slide 20: End to End Testing

## Slide 21: In EHV protection, a circuit breaker can be tripped by a number of different protection schemes located on different panels within the substation
Primary Bus Protection
Secondary Bus Protection
Primary 1 Line Protection
Primary 2 Line Protection
Backup Electromechanical Line Prot.

## Slide 22
Modern test sets which include synchronized testing capability via GPS can be used within the substation to scheme test the breaker failure relay with the initiating protection schemes

## Slide 23
Operation of the protective relay breaker failure initiating contact (BFI or 62-X) and the confirmation of the correct wiring to the BFR.
Operation of the BFR re-trip element if used.
Operation and time delay of the BFR timer.
Blocking of circuit breaker re-closing.
Operation of the BFR lockout relay.
Operation of Local and SCADA alarms.
Pallet Interlocks

## Slide 24
The scheme test can be repeated for an internal fault with increasing circuit breaker clearing times to measure the total margin in the BFR timer setting. With this type of test, all the elements affecting the performance of the BFR are tested simultaneously.

## Slide 25: Questions ?