## Slide 1: BF Scheme Design Considerations Standard Sections 8 & 9
Breaker Failure Tutorial
PES GM
July 2010

## Slide 2: Of course the scheme should….
Operate only when expected and desired.
Operate independently of the type of failure in the breaker (but note prior rules on use of 52a contact).
Have proper application of auxiliary relays (avoid when you can, use only for isolation, and watch pickup and dropout time delay impact).
Have test switches arranged to allow safe overall testing of the scheme (testing BF tripping is a risk that some avoid).

## Slide 3: The scheme should…
Be able to operate when the dc source to the failed breaker is lost
Use proper application of dc circuits to avoid mixing supply sources.
This means that failure of the dc to any one of the redundant zone protective relays must not disable BF protection.
  There are two ways to meet this need…

## Slide 4: BF operation when dc to zone relay is lost
The traditional approach:
  A BF scheme is associated with the breaker and its control panel (not with adjacent line, bus, transformer zones or relay panels.
  This BF scheme has its own relays and its own separately-fused dc supply.
  BFI comes from multiple adjacent zones by isolated contacts or isolated electronic inputs to avoid mixing dc from those panels.
  This approach implied in NERC Planning Standards and many regional design requirements.
  Monitor the dc to the BF scheme (µP relays do this).

## Slide 5: BF operation when dc to zone relay is lost
The new microprocessor relay approach:
  A BF scheme is included as a function inside a zone relay (line, bus, transformer).
  This BF scheme is dependent on the zone relay and its dc supply.
  To avoid loss of BF protection when zone relay or its dc fails, at least 2 redundant relays must each have parallel independent BF schemes inside.
  Criterion – loss of zone relay or its dc does not disable BF protection.
  For ring buses and 1½ breaker buses, each relay needs 2 independent BF functions and separated breaker current inputs (available in newest relays).
  Zone relays report dc failures.

## Slide 6: The scheme should…
Minimize the impact of dc transients
  This is beyond SWC and is a special BF risk.
  Battery grounding problem - Battery is grounded at center tap between two monitoring lamps or resistors - battery leads are +/- Vdc/2 with respect to ground.
+ 62 Vdc
- 62 Vdc

## Slide 7: The scheme should…
Minimize the impact of dc transients
  Capacitance of BFI input wiring
  Accidental battery supply lead grounding suddenly shifts ground potential. Also, other spikes/surges.
  Relay BFI input spike decays according to input impedance.
  If BFI input responds, BF timing may pick up and seal in causing false BF trip.
  Modern secure BFI inputs will completely avoid pickup on Vdc/2, or on Vdc coupled through 1 to 4 uF.
BUFFER
62X
Long wiring run
BFI

## Slide 8: Tripping Actions
Traditional – operate a lockout switch to:
  Trip all other breakers to isolate the failed breaker; keep trip circuits closed.
    Trip all adjacent zone breakers; some of this is redundant.
  Transfer trip remote breakers
  Stop carrier, or
  Close line grounding switch (pyrotechnic or spring-operated). Slow clearing, and applies new fault to system.
  Both of latter two have reclosing problem.

## Slide 9: Tripping Actions
Traditional –lockout switch continued:
  Block closing of failed breaker and all tripped breakers.
  Drive reclosing relay to “lockout” (end of sequence) state.
  Latch and alarm the failed-breaker state.
  Require overt human action before any surrounding breakers can be closed.
  Indicate the BF state independently of any other overlapping lockouts (e.g. transformer fault).

## Slide 10: Tripping Actions
Newest relays with built-in BF:
  Use data messaging among relays or auxiliary control devices on optical fiber communications links.
  Use mechanical or electrical latching of output relays to hold trip circuits and block close circuits.
  Depend on programmed scheme logic and/or station computer to keep track of trip and lockout topology of substation for multiple conditions, e.g. transformer fault with breaker failure.
  Multiple lockout actions must be cleared separately.
  Be aware of volatility of trip/lockout mapping – what happens when relay dc goes away and comes back?
  Saves wiring; easier and safer to verify.

## Slide 11: Using Bus Tripping for BF
If any breaker on the bus fails for an adjacent zone fault, the bus must be stripped.
Bus differential lockout switch or distributed tripping modules can be used to get bus breakers tripped.
Still need BF lockout switch on each breaker or equivalent to distinguish BF trip from bus fault, and to trip adjacent-zone or remote breakers.
Beware of common failure points or shared dc between bus protection and BF protection.

## Slide 12: More recommendations
No cascaded BF protection (initiating BF on a breaker that is tripped by another BF scheme) – 2 scheme malfunctions are more likely than 2 sequential breaker failures, and tear the power system apart.
No BF initiation for manual or SCADA trips – only for trips by fault-detecting relays.
Use retrip to minimize the impact of a false BFI with seal-in through maintenance error or battery ground.
Caution – if BF Initiate comes from lockout switch or latched relay (bus or xfmr fault), it will be sustained until that zone lockout is reset. (watch when reenergizing; scheme design.)

## Slide 13: Current Detectors
Non-directional overcurrent element monitors breaker current.
Measure each breaker separately - do not use line or winding currents in a ring bus or 1½ breaker bus.
Key performance factor for traditional logic – fast dropout when fault clears.
For new control timer logic – dropout doesn’t matter; stable pickup time can be slower without delaying BF tripping .

## Slide 14: Current Detector Settings
Phase current detectors (50BF) – at least 2 phases, 3 is better.
Set above max. load if possible for false trip avoidance, but…
Set well below minimum phase fault current (50%).
Negative sequence current detector can supplement phase current detectors (don’t forget 3-phase faults).

## Slide 15: Current Detector Settings
Ground current detector – residual connection or calculation (~ zero sequence).
Load is not a problem.
Set well below minimum ground fault current (30-40%).
Or, set it at least below the most sensitive ground fault relay that may trip.
Very low settings - watch for decaying transient in ct circuit.

## Slide 16: Sensitive Fault Detection
BFI
62X
62Y
Optional input
for adjacent
transformer zone
internal fault
sensitivity with
stuck breaker
Don’t use 52a
by itself, with or instead of 50.
86T
52a
62
50
50G
AND
BUFFER
BUFFER
OR
IA
IB
IC
3I0
OR
86BF
86
BF
BUFFER
dc+
Seal-in
dc-

## Slide 17: Timer setting – Traditional Scheme
Typical margin – 3 to 10 cycles.
Stay within CFC time on bulk transmission.

## Slide 18: BF Timer setting – Control Timer Scheme with 50 pickup
50 reset time is removed – get more margin or set shorter delay
50 pickup time adds to 62 BF time here (set 62 lower)
Control timer setting not critical, but set below reclosing time.

## Slide 19: Breaker and CT fault protection
Bus
B, BF L
Stub or bushing
Line
Faults detected by line or bus relay, but not isolated by breaker.
BF scheme must trip/transfer trip adjacent breakers to isolate the fault in BF time.
Apparatus frame-ground CT with 50 relay direct-trips 86BF - can speed up clearing to primary time - helpful but usually not essential.
Live-tank
breaker
CTs, e.g. free-
standing EHV