## Sheet1
CONTENTS
Sheet 1: | CALCULATOR (this sheet) | [9 empty] | A document of the
Sheet 2: | INSTRUCTIONS |  |  |  |  | Excel Spread Sheet |  |  |  |  | IEEE Power Systems Relaying Committee
Sheet 4: | BACKGROUND |  |  |  |  | See IEEE publication C37.110: "IEEE Guide for the Application |  |  |  |  | Contact: gswift@nxtphase.com
[6 empty] | of CurrentTransformers Used for Protective Relaying Purposes" |  |  |  |  | Refer also to "CT SAT Theory (PSRC)".
ASSUMPTIONS: |  | CT core losses and sec'y reactance zero (thru-hole primary). | [5 empty] | Frequency: 60 Hz
|  | CT primary current is zero for t<0. |  |  |  | CT is 5 amp nominal |  | Time step = 1/12,000 second.
INPUT PARAMETERS: |  |  |  | ENTER: | [6 empty] | CALCULATED:
|  | Inverse of sat. curve slope = | S = | 22 | --- |  |  |  |  | Rt = | Total burden resistance = Rw + Rb = |  |  | 4 | ohms
|  | RMS voltage at 10A exc. current = | Vs = | 400 | volts rms |  |  |  |  | pf = | Total burden power factor = |  |  | 0.89443 | --- | CALCULATION OF RP
|  | Turns ratio = n2/1= | N = | 240 | --- |  |  |  |  | Zb = | Total burden impedance = |  |  | 4.4721 | ohms
|  | Winding resistance = | Rw = | 0 | ohms |  |  |  |  | Tau1 = | System time constant = |  |  | 0.031831 | seconds | S = | 22
|  | Burden resistance = | Rb = | 4 | ohms |  |  |  |  | Lamsat = | Peak flux-linkages corresponding to Vs |  |  | 1.5006 | Wb-turns | INDEX = | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
|  | Burden reactance = | Xb = | 2 | ohms |  |  |  |  | w = | Radian freq = |  |  | 376.9911 | rad/s | ANGLE = | 0 | 0.015708 | 0.031416 | 0.047124 | 0.062832 | 0.07854 | 0.094248 | 0.10996 | 0.12566 | 0.14137 | 0.15708 | 0.17279 | 0.1885 | 0.2042 | 0.21991 | 0.23562 | 0.25133 | 0.26704 | 0.28274 | 0.29845 | 0.31416 | 0.32987 | 0.34558 | 0.36128 | 0.37699 | 0.3927 | 0.40841 | 0.42412 | 0.43982 | 0.45553 | 0.47124 | 0.48695 | 0.50265 | 0.51836 | 0.53407 | 0.54978 | 0.56549 | 0.58119 | 0.5969 | 0.61261 | 0.62832 | 0.64403 | 0.65973 | 0.67544 | 0.69115 | 0.70686 | 0.72257 | 0.73827 | 0.75398 | 0.76969 | 0.7854 | 0.80111 | 0.81681 | 0.83252 | 0.84823 | 0.86394 | 0.87965 | 0.89535 | 0.91106 | 0.92677 | 0.94248 | 0.95819 | 0.97389 | 0.9896 | 1.0053 | 1.021 | 1.0367 | 1.0524 | 1.0681 | 1.0838 | 1.0996 | 1.1153 | 1.131 | 1.1467 | 1.1624 | 1.1781 | 1.1938 | 1.2095 | 1.2252 | 1.2409 | 1.2566 | 1.2723 | 1.2881 | 1.3038 | 1.3195 | 1.3352 | 1.3509 | 1.3666 | 1.3823 | 1.398 | 1.4137 | 1.4294 | 1.4451 | 1.4608 | 1.4765 | 1.4923 | 1.508 | 1.5237 | 1.5394 | 1.5551 | 1.5708
|  | System X/R ratio = | XoverR = | 12 | --- |  |  |  |  | RP = | Rms-to-peak ratio = |  |  | 0.34584 |  | (SINE^S)^2 = | 0 | 4.251e-80 | 7.4379e-67 | 4.1261e-59 | 1.2804e-53 | 2.3137e-49 | 6.9124e-46 | 5.9575e-43 | 2.065e-40 | 3.5666e-38 | 3.5533e-36 | 2.2666e-34 | 9.999e-33 | 3.2344e-31 | 8.0286e-30 | 1.5854e-28 | 2.5642e-27 | 3.4784e-26 | 4.0362e-25 | 4.0729e-24 | 3.6243e-23 | 2.8781e-22 | 2.0607e-21 | 1.3421e-20 | 8.0125e-20 | 4.4151e-19 | 2.2589e-18 | 1.0788e-17 | 4.8319e-17 | 2.0383e-16 | 8.1294e-16 | 3.0758e-15 | 1.1074e-14 | 3.8048e-14 | 1.2507e-13 | 3.9423e-13 | 1.1942e-12 | 3.4832e-12 | 9.8001e-12 | 2.6642e-11 | 7.0085e-11 | 1.7866e-10 | 4.4194e-10 | 1.062e-09 | 2.4823e-09 | 5.6488e-09 | 1.2528e-08 | 2.7103e-08 | 5.7246e-08 | 1.1814e-07 | 2.3842e-07 | 4.708e-07 | 9.1031e-07 | 1.7245e-06 | 3.2028e-06 | 5.8345e-06 | 1.0431e-05 | 1.8311e-05 | 3.1575e-05 | 5.3509e-05 | 8.9153e-05 | 0.0001461 | 0.00023556 | 0.00037383 | 0.0005841 | 0.00089887 | 0.0013627 | 0.0020359 | 0.0029983 | 0.0043534 | 0.0062339 | 0.0088053 | 0.012271 | 0.016876 | 0.022907 | 0.030696 | 0.040612 | 0.053062 | 0.068473 | 0.087284 | 0.10992 | 0.13678 | 0.16818 | 0.20438 | 0.24548 | 0.29147 | 0.34211 | 0.397 | 0.45551 | 0.51679 | 0.5798 | 0.64329 | 0.70587 | 0.76604 | 0.82225 | 0.87298 | 0.91676 | 0.9523 | 0.97852 | 0.99459 | 1
|  | Per unit offset in primary current = | Off = | 1 | -1<Off<1 |  |  |  |  | A = | Coefficient in instantaneous ie
|  | Per unit remanence (based on Vs) = | lrem | 0 | --- | [5 empty] | versus lambda curve: ie = A * l^S : |  |  | 0.003835 | --- | RP = | 22 0: 0.34584
|  | Symmetrical primary fault current = | Ip = | 12000 | amps rms |  |  |  |  | dt = | Time step = |  |  | 8.3333e-05 | seconds
[10 empty] | Lb = | Burden inductance = |  |  | 0.0053052 | henries
|  | Thick lines: | Ideal (blue) and actual (black) secondary current in amps vs time in seconds.
|  | Thin lines: | Ideal (blue) and actual (black) secondary current extracted fundamental rms value, using a simple DFT with a one-cycle window.
To determine the effect of saturation on a particular digital relay, one must have "models" for the blocks shown below:
[9 empty] | Calculation of Mag. Of Fund'l |  |  | Calculation of Mag. Of Fund'l |  | Phase | Phase
|  | is = | [6 empty] | IDEAL |  |  | ACTUAL |  | IDEAL | ACTUAL
step | time | pri cur/N | fl-linkages | exc curr |  | sec cur | d/dt(is)
number | t | i1(t)/N | l(t) | ie(t) | Dl(t) | i2(t) |  | I1(t)*sin | I1(t)*cos | I1MAG | I2(t)*sin | I2(t)*cos | I2MAG | I1PH | I2PH
| seconds | amps | Wb-turns | amps | Wb-turns | amps | amps/s
| TIME | IDEAL |  |  |  | ACTUAL
-200 | -0.016667 | 0 | 0.0001 | 3.835e-91 | -0.0016579 | -3.835e-91 | -3749.9877 |  |  | 0 |  |  | 0 | 0 | 0
-199 | -0.016583 | 0 | 0.0001 | 3.835e-91 | -0.0012833 | -3.835e-91 | -2902.8592 |  |  | 0 |  |  | 0 | 0 | 0
-198 | -0.0165 | 0 | 0.0001 | 3.835e-91 | -0.00090921 | -3.835e-91 | -2056.5827 |  |  | 0 |  |  | 0 | 0 | 0
-197 | -0.016417 | 0 | 0.0001 | 3.835e-91 | -0.00053581 | -3.835e-91 | -1211.9837 |  |  | 0 |  |  | 0 | 0 | 0
-196 | -0.016333 | 0 | 0.0001 | 3.835e-91 | -0.00016353 | -3.835e-91 | -369.8859 |  |  | 0 |  |  | 0 | 0 | 0
-195 | -0.01625 | 0 | 0.0001 | 3.835e-91 | 0.00020729 | -3.835e-91 | 468.8893 |  |  | 0 |  |  | 0 | 0 | 0
-194 | -0.016167 | 0 | 0.0001 | 3.835e-91 | 0.00057628 | -3.835e-91 | 1303.5237 |  |  | 0 |  |  | 0 | 0 | 0
-193 | -0.016083 | 0 | 0.0001 | 3.835e-91 | 0.00094308 | -3.835e-91 | 2133.2032 |  |  | 0 |  |  | 0 | 0 | 0
-192 | -0.016 | 0 | 0.0001 | 3.835e-91 | 0.0013073 | -3.835e-91 | 2957.1188 |  |  | 0 |  |  | 0 | 0 | 0
-191 | -0.015917 | 0 | 0.0001 | 3.835e-91 | 0.0016687 | -3.835e-91 | 3774.4667 |  |  | 0 |  |  | 0 | 0 | 0
-190 | -0.015833 | 0 | 0.0001 | 3.835e-91 | 0.0020268 | -3.835e-91 | 4584.4501 |  |  | 0 |  |  | 0 | 0 | 0
-189 | -0.01575 | 0 | 0.0001 | 3.835e-91 | 0.0023813 | -3.835e-91 | 5386.2789 |  |  | 0 |  |  | 0 | 0 | 0
-188 | -0.015667 | 0 | 0.0001 | 3.835e-91 | 0.0027318 | -3.835e-91 | 6179.1714 |  |  | 0 |  |  | 0 | 0 | 0
-187 | -0.015583 | 0 | 0.0001 | 3.835e-91 | 0.003078 | -3.835e-91 | 6962.3546 |  |  | 0 |  |  | 0 | 0 | 0
-186 | -0.0155 | 0 | 0.0001 | 3.835e-91 | 0.0034196 | -3.835e-91 | 7735.065 |  |  | 0 |  |  | 0 | 0 | 0
-185 | -0.015417 | 0 | 0.0001 | 3.835e-91 | 0.0037563 | -3.835e-91 | 8496.5494 |  |  | 0 |  |  | 0 | 0 | 0
-184 | -0.015333 | 0 | 0.0001 | 3.835e-91 | 0.0040877 | -3.835e-91 | 9246.0658 |  |  | 0 |  |  | 0 | 0 | 0
-183 | -0.01525 | 0 | 0.0001 | 3.835e-91 | 0.0044134 | -3.835e-91 | 9982.8838 |  |  | 0 |  |  | 0 | 0 | 0
-182 | -0.015167 | 0 | 0.0001 | 3.835e-91 | 0.0047332 | -3.835e-91 | 10706.2856 |  |  | 0 |  |  | 0 | 0 | 0
-181 | -0.015083 | 0 | 0.0001 | 3.835e-91 | 0.0050468 | -3.835e-91 | 11415.5667 |  |  | 0 |  |  | 0 | 0 | 0
-180 | -0.015 | 0 | 0.0001 | 3.835e-91 | 0.0053538 | -3.835e-91 | 12110.0363 |  |  | 0 |  |  | 0 | 0 | 0
-179 | -0.014917 | 0 | 0.0001 | 3.835e-91 | 0.005654 | -3.835e-91 | 12789.0184 |  |  | 0 |  |  | 0 | 0 | 0
-178 | -0.014833 | 0 | 0.0001 | 3.835e-91 | 0.005947 | -3.835e-91 | 13451.8521 |  |  | 0 |  |  | 0 | 0 | 0
-177 | -0.01475 | 0 | 0.0001 | 3.835e-91 | 0.0062326 | -3.835e-91 | 14097.8926 |  |  | 0 |  |  | 0 | 0 | 0
-176 | -0.014667 | 0 | 0.0001 | 3.835e-91 | 0.0065105 | -3.835e-91 | 14726.5114 |  |  | 0 |  |  | 0 | 0 | 0
-175 | -0.014583 | 0 | 0.0001 | 3.835e-91 | 0.0067805 | -3.835e-91 | 15337.0974 |  |  | 0 |  |  | 0 | 0 | 0
-174 | -0.0145 | 0 | 0.0001 | 3.835e-91 | 0.0070422 | -3.835e-91 | 15929.0571 |  |  | 0 |  |  | 0 | 0 | 0
-173 | -0.014417 | 0 | 0.0001 | 3.835e-91 | 0.0072954 | -3.835e-91 | 16501.8155 |  |  | 0 |  |  | 0 | 0 | 0
-172 | -0.014333 | 0 | 0.0001 | 3.835e-91 | 0.0075399 | -3.835e-91 | 17054.8164 |  |  | 0 |  |  | 0 | 0 | 0
-171 | -0.01425 | 0 | 0.0001 | 3.835e-91 | 0.0077754 | -3.835e-91 | 17587.5232 |  |  | 0 |  |  | 0 | 0 | 0
-170 | -0.014167 | 0 | 0.0001 | 3.835e-91 | 0.0080017 | -3.835e-91 | 18099.4192 |  |  | 0 |  |  | 0 | 0 | 0
-169 | -0.014083 | 0 | 0.0001 | 3.835e-91 | 0.0082186 | -3.835e-91 | 18590.0082 |  |  | 0 |  |  | 0 | 0 | 0
-168 | -0.014 | 0 | 0.0001 | 3.835e-91 | 0.0084258 | -3.835e-91 | 19058.8152 |  |  | 0 |  |  | 0 | 0 | 0
-167 | -0.013917 | 0 | 0.0001 | 3.835e-91 | 0.0086233 | -3.835e-91 | 19505.3863 |  |  | 0 |  |  | 0 | 0 | 0
-166 | -0.013833 | 0 | 0.0001 | 3.835e-91 | 0.0088107 | -3.835e-91 | 19929.29 |  |  | 0 |  |  | 0 | 0 | 0
-165 | -0.01375 | 0 | 0.0001 | 3.835e-91 | 0.0089879 | -3.835e-91 | 20330.1167 |  |  | 0 |  |  | 0 | 0 | 0
-164 | -0.013667 | 0 | 0.0001 | 3.835e-91 | 0.0091547 | -3.835e-91 | 20707.4798 |  |  | 0 |  |  | 0 | 0 | 0
-163 | -0.013583 | 0 | 0.0001 | 3.835e-91 | 0.009311 | -3.835e-91 | 21061.0159 |  |  | 0 |  |  | 0 | 0 | 0
-162 | -0.0135 | 0 | 0.0001 | 3.835e-91 | 0.0094566 | -3.835e-91 | 21390.3848 |  |  | 0 |  |  | 0 | 0 | 0
-161 | -0.013417 | 0 | 0.0001 | 3.835e-91 | 0.0095914 | -3.835e-91 | 21695.2704 |  |  | 0 |  |  | 0 | 0 | 0
-160 | -0.013333 | 0 | 0.0001 | 3.835e-91 | 0.0097153 | -3.835e-91 | 21975.3806 |  |  | 0 |  |  | 0 | 0 | 0
-159 | -0.01325 | 0 | 0.0001 | 3.835e-91 | 0.009828 | -3.835e-91 | 22230.4478 |  |  | 0 |  |  | 0 | 0 | 0
-158 | -0.013167 | 0 | 0.0001 | 3.835e-91 | 0.0099296 | -3.835e-91 | 22460.2289 |  |  | 0 |  |  | 0 | 0 | 0
-157 | -0.013083 | 0 | 0.0001 | 3.835e-91 | 0.01002 | -3.835e-91 | 22664.5061 |  |  | 0 |  |  | 0 | 0 | 0
-156 | -0.013 | 0 | 0.0001 | 3.835e-91 | 0.010099 | -3.835e-91 | 22843.0864 |  |  | 0 |  |  | 0 | 0 | 0
-155 | -0.012917 | 0 | 0.0001 | 3.835e-91 | 0.010166 | -3.835e-91 | 22995.8023 |  |  | 0 |  |  | 0 | 0 | 0
-154 | -0.012833 | 0 | 0.0001 | 3.835e-91 | 0.010222 | -3.835e-91 | 23122.5118 |  |  | 0 |  |  | 0 | 0 | 0
-153 | -0.01275 | 0 | 0.0001 | 3.835e-91 | 0.010267 | -3.835e-91 | 23223.0985 |  |  | 0 |  |  | 0 | 0 | 0
-152 | -0.012667 | 0 | 0.0001 | 3.835e-91 | 0.0103 | -3.835e-91 | 23297.4717 |  |  | 0 |  |  | 0 | 0 | 0
-151 | -0.012583 | 0 | 0.0001 | 3.835e-91 | 0.010321 | -3.835e-91 | 23345.5667 |  |  | 0 |  |  | 0 | 0 | 0
-150 | -0.0125 | 0 | 0.0001 | 3.835e-91 | 0.010331 | -3.835e-91 | 23367.3447 |  |  | 0 |  |  | 0 | 0 | 0
-149 | -0.012417 | 0 | 0.0001 | 3.835e-91 | 0.010329 | -3.835e-91 | 23362.7926 |  |  | 0 |  |  | 0 | 0 | 0
-148 | -0.012333 | 0 | 0.0001 | 3.835e-91 | 0.010315 | -3.835e-91 | 23331.9235 |  |  | 0 |  |  | 0 | 0 | 0
-147 | -0.01225 | 0 | 0.0001 | 3.835e-91 | 0.01029 | -3.835e-91 | 23274.7764 |  |  | 0 |  |  | 0 | 0 | 0
-146 | -0.012167 | 0 | 0.0001 | 3.835e-91 | 0.010253 | -3.835e-91 | 23191.4163 |  |  | 0 |  |  | 0 | 0 | 0
-145 | -0.012083 | 0 | 0.0001 | 3.835e-91 | 0.010204 | -3.835e-91 | 23081.9338 |  |  | 0 |  |  | 0 | 0 | 0
-144 | -0.012 | 0 | 0.0001 | 3.835e-91 | 0.010145 | -3.835e-91 | 22946.4455 |  |  | 0 |  |  | 0 | 0 | 0
-143 | -0.011917 | 0 | 0.0001 | 3.835e-91 | 0.010073 | -3.835e-91 | 22785.0935 |  |  | 0 |  |  | 0 | 0 | 0
-142 | -0.011833 | 0 | 0.0001 | 3.835e-91 | 0.0099905 | -3.835e-91 | 22598.0454 |  |  | 0 |  |  | 0 | 0 | 0
-141 | -0.01175 | 0 | 0.0001 | 3.835e-91 | 0.0098966 | -3.835e-91 | 22385.4943 |  |  | 0 |  |  | 0 | 0 | 0
-140 | -0.011667 | 0 | 0.0001 | 3.835e-91 | 0.0097914 | -3.835e-91 | 22147.6583 |  |  | 0 |  |  | 0 | 0 | 0
-139 | -0.011583 | 0 | 0.0001 | 3.835e-91 | 0.0096752 | -3.835e-91 | 21884.7804 |  |  | 0 |  |  | 0 | 0 | 0
-138 | -0.0115 | 0 | 0.0001 | 3.835e-91 | 0.009548 | -3.835e-91 | 21597.1284 |  |  | 0 |  |  | 0 | 0 | 0
-137 | -0.011417 | 0 | 0.0001 | 3.835e-91 | 0.00941 | -3.835e-91 | 21284.9946 |  |  | 0 |  |  | 0 | 0 | 0
-136 | -0.011333 | 0 | 0.0001 | 3.835e-91 | 0.0092614 | -3.835e-91 | 20948.6951 |  |  | 0 |  |  | 0 | 0 | 0
-135 | -0.01125 | 0 | 0.0001 | 3.835e-91 | 0.0091021 | -3.835e-91 | 20588.5701 |  |  | 0 |  |  | 0 | 0 | 0
-134 | -0.011167 | 0 | 0.0001 | 3.835e-91 | 0.0089326 | -3.835e-91 | 20204.9834 |  |  | 0 |  |  | 0 | 0 | 0
-133 | -0.011083 | 0 | 0.0001 | 3.835e-91 | 0.0087528 | -3.835e-91 | 19798.3216 |  |  | 0 |  |  | 0 | 0 | 0
-132 | -0.011 | 0 | 0.0001 | 3.835e-91 | 0.008563 | -3.835e-91 | 19368.9944 |  |  | 0 |  |  | 0 | 0 | 0
-131 | -0.010917 | 0 | 0.0001 | 3.835e-91 | 0.0083633 | -3.835e-91 | 18917.4334 |  |  | 0 |  |  | 0 | 0 | 0
-130 | -0.010833 | 0 | 0.0001 | 3.835e-91 | 0.0081541 | -3.835e-91 | 18444.0927 |  |  | 0 |  |  | 0 | 0 | 0
-129 | -0.01075 | 0 | 0.0001 | 3.835e-91 | 0.0079354 | -3.835e-91 | 17949.4473 |  |  | 0 |  |  | 0 | 0 | 0
-128 | -0.010667 | 0 | 0.0001 | 3.835e-91 | 0.0077075 | -3.835e-91 | 17433.9936 |  |  | 0 |  |  | 0 | 0 | 0
-127 | -0.010583 | 0 | 0.0001 | 3.835e-91 | 0.0074707 | -3.835e-91 | 16898.2484 |  |  | 0 |  |  | 0 | 0 | 0
-126 | -0.0105 | 0 | 0.0001 | 3.835e-91 | 0.0072251 | -3.835e-91 | 16342.7484 |  |  | 0 |  |  | 0 | 0 | 0
-125 | -0.010417 | 0 | 0.0001 | 3.835e-91 | 0.006971 | -3.835e-91 | 15768.05 |  |  | 0 |  |  | 0 | 0 | 0
-124 | -0.010333 | 0 | 0.0001 | 3.835e-91 | 0.0067087 | -3.835e-91 | 15174.7282 |  |  | 0 |  |  | 0 | 0 | 0
-123 | -0.01025 | 0 | 0.0001 | 3.835e-91 | 0.0064384 | -3.835e-91 | 14563.3767 |  |  | 0 |  |  | 0 | 0 | 0
-122 | -0.010167 | 0 | 0.0001 | 3.835e-91 | 0.0061604 | -3.835e-91 | 13934.6067 |  |  | 0 |  |  | 0 | 0 | 0
-121 | -0.010083 | 0 | 0.0001 | 3.835e-91 | 0.005875 | -3.835e-91 | 13289.0467 |  |  | 0 |  |  | 0 | 0 | 0
-120 | -0.01 | 0 | 0.0001 | 3.835e-91 | 0.0055825 | -3.835e-91 | 12627.3418 |  |  | 0 |  |  | 0 | 0 | 0
-119 | -0.0099167 | 0 | 0.0001 | 3.835e-91 | 0.0052831 | -3.835e-91 | 11950.153 |  |  | 0 |  |  | 0 | 0 | 0
-118 | -0.0098333 | 0 | 0.0001 | 3.835e-91 | 0.0049772 | -3.835e-91 | 11258.1563 |  |  | 0 |  |  | 0 | 0 | 0
-117 | -0.00975 | 0 | 0.0001 | 3.835e-91 | 0.004665 | -3.835e-91 | 10552.0427 |  |  | 0 |  |  | 0 | 0 | 0
-116 | -0.0096667 | 0 | 0.0001 | 3.835e-91 | 0.0043469 | -3.835e-91 | 9832.5167 |  |  | 0 |  |  | 0 | 0 | 0
-115 | -0.0095833 | 0 | 0.0001 | 3.835e-91 | 0.0040232 | -3.835e-91 | 9100.2965 |  |  | 0 |  |  | 0 | 0 | 0
-114 | -0.0095 | 0 | 0.0001 | 3.835e-91 | 0.0036942 | -3.835e-91 | 8356.1123 |  |  | 0 |  |  | 0 | 0 | 0
-113 | -0.0094167 | 0 | 0.0001 | 3.835e-91 | 0.0033602 | -3.835e-91 | 7600.7064 |  |  | 0 |  |  | 0 | 0 | 0
-112 | -0.0093333 | 0 | 0.0001 | 3.835e-91 | 0.0030217 | -3.835e-91 | 6834.8321 |  |  | 0 |  |  | 0 | 0 | 0
-111 | -0.00925 | 0 | 0.0001 | 3.835e-91 | 0.0026788 | -3.835e-91 | 6059.253 |  |  | 0 |  |  | 0 | 0 | 0
-110 | -0.0091667 | 0 | 0.0001 | 3.835e-91 | 0.0023319 | -3.835e-91 | 5274.7422 |  |  | 0 |  |  | 0 | 0 | 0
-109 | -0.0090833 | 0 | 0.0001 | 3.835e-91 | 0.0019815 | -3.835e-91 | 4482.0816 |  |  | 0 |  |  | 0 | 0 | 0
-108 | -0.009 | 0 | 0.0001 | 3.835e-91 | 0.0016278 | -3.835e-91 | 3682.0612 |  |  | 0 |  |  | 0 | 0 | 0
-107 | -0.0089167 | 0 | 0.0001 | 3.835e-91 | 0.0012712 | -3.835e-91 | 2875.4782 |  |  | 0 |  |  | 0 | 0 | 0
-106 | -0.0088333 | 0 | 0.0001 | 3.835e-91 | 0.00091211 | -3.835e-91 | 2063.1363 |  |  | 0 |  |  | 0 | 0 | 0
-105 | -0.00875 | 0 | 0.0001 | 3.835e-91 | 0.00055078 | -3.835e-91 | 1245.8447 |  |  | 0 |  |  | 0 | 0 | 0
-104 | -0.0086667 | 0 | 0.0001 | 3.835e-91 | 0.00018763 | -3.835e-91 | 424.4177 |  |  | 0 |  |  | 0 | 0 | 0
-103 | -0.0085833 | 0 | 0.0001 | 3.835e-91 | -0.00017698 | -3.835e-91 | -400.3265 |  |  | 0 |  |  | 0 | 0 | 0
-102 | -0.0085 | 0 | 0.0001 | 3.835e-91 | -0.0005427 | -3.835e-91 | -1227.5664 |  |  | 0 |  |  | 0 | 0 | 0
-101 | -0.0084167 | 0 | 0.0001 | 3.835e-91 | -0.00090916 | -3.835e-91 | -2056.478 |  |  | 0 |  |  | 0 | 0 | 0
-100 | -0.0083333 | 0 | 0.0001 | 3.835e-91 | -0.001276 | -3.835e-91 | -2886.2358 |  |  | 0 |  |  | 0 | 0 | 0
-99 | -0.00825 | 0 | 0.0001 | 3.835e-91 | -0.0016428 | -3.835e-91 | -3716.0134 |  |  | 0 |  |  | 0 | 0 | 0
-98 | -0.0081667 | 0 | 0.0001 | 3.835e-91 | -0.0020093 | -3.835e-91 | -4544.9844 |  |  | 0 |  |  | 0 | 0 | 0
-97 | -0.0080833 | 0 | 0.0001 | 3.835e-91 | -0.0023751 | -3.835e-91 | -5372.3231 |  |  | 0 |  |  | 0 | 0 | 0
-96 | -0.008 | 0 | 0.0001 | 3.835e-91 | -0.0027398 | -3.835e-91 | -6197.2058 |  |  | 0 |  |  | 0 | 0 | 0
-95 | -0.0079167 | 0 | 0.0001 | 3.835e-91 | -0.003103 | -3.835e-91 | -7018.8109 |  |  | 0 |  |  | 0 | 0 | 0
-94 | -0.0078333 | 0 | 0.0001 | 3.835e-91 | -0.0034644 | -3.835e-91 | -7836.32 |  |  | 0 |  |  | 0 | 0 | 0
-93 | -0.00775 | 0 | 0.0001 | 3.835e-91 | -0.0038237 | -3.835e-91 | -8648.9191 |  |  | 0 |  |  | 0 | 0 | 0
-92 | -0.0076667 | 0 | 0.0001 | 3.835e-91 | -0.0041804 | -3.835e-91 | -9455.7989 |  |  | 0 |  |  | 0 | 0 | 0
-91 | -0.0075833 | 0 | 0.0001 | 3.835e-91 | -0.0045342 | -3.835e-91 | -10256.1556 |  |  | 0 |  |  | 0 | 0 | 0
-90 | -0.0075 | 0 | 0.0001 | 3.835e-91 | -0.0048848 | -3.835e-91 | -11049.1921 |  |  | 0 |  |  | 0 | 0 | 0
-89 | -0.0074167 | 0 | 0.0001 | 3.835e-91 | -0.0052318 | -3.835e-91 | -11834.1184 |  |  | 0 |  |  | 0 | 0 | 0
-88 | -0.0073333 | 0 | 0.0001 | 3.835e-91 | -0.0055749 | -3.835e-91 | -12610.1526 |  |  | 0 |  |  | 0 | 0 | 0
-87 | -0.00725 | 0 | 0.0001 | 3.835e-91 | -0.0059137 | -3.835e-91 | -13376.5215 |  |  | 0 |  |  | 0 | 0 | 0
-86 | -0.0071667 | 0 | 0.0001 | 3.835e-91 | -0.0062479 | -3.835e-91 | -14132.4616 |  |  | 0 |  |  | 0 | 0 | 0
-85 | -0.0070833 | 0 | 0.0001 | 3.835e-91 | -0.0065772 | -3.835e-91 | -14877.2196 |  |  | 0 |  |  | 0 | 0 | 0
-84 | -0.007 | 0 | 0.0001 | 3.835e-91 | -0.0069012 | -3.835e-91 | -15610.0533 |  |  | 0 |  |  | 0 | 0 | 0
-83 | -0.0069167 | 0 | 0.0001 | 3.835e-91 | -0.0072195 | -3.835e-91 | -16330.2322 |  |  | 0 |  |  | 0 | 0 | 0
-82 | -0.0068333 | 0 | 0.0001 | 3.835e-91 | -0.007532 | -3.835e-91 | -17037.0384 |  |  | 0 |  |  | 0 | 0 | 0
-81 | -0.00675 | 0 | 0.0001 | 3.835e-91 | -0.0078383 | -3.835e-91 | -17729.7673 |  |  | 0 |  |  | 0 | 0 | 0
-80 | -0.0066667 | 0 | 0.0001 | 3.835e-91 | -0.008138 | -3.835e-91 | -18407.728 |  |  | 0 |  |  | 0 | 0 | 0
-79 | -0.0065833 | 0 | 0.0001 | 3.835e-91 | -0.0084309 | -3.835e-91 | -19070.2444 |  |  | 0 |  |  | 0 | 0 | 0
-78 | -0.0065 | 0 | 0.0001 | 3.835e-91 | -0.0087167 | -3.835e-91 | -19716.6554 |  |  | 0 |  |  | 0 | 0 | 0
-77 | -0.0064167 | 0 | 0.0001 | 3.835e-91 | -0.008995 | -3.835e-91 | -20346.3161 |  |  | 0 |  |  | 0 | 0 | 0
-76 | -0.0063333 | 0 | 0.0001 | 3.835e-91 | -0.0092657 | -3.835e-91 | -20958.598 |  |  | 0 |  |  | 0 | 0 | 0
-75 | -0.00625 | 0 | 0.0001 | 3.835e-91 | -0.0095285 | -3.835e-91 | -21552.8897 |  |  | 0 |  |  | 0 | 0 | 0
-74 | -0.0061667 | 0 | 0.0001 | 3.835e-91 | -0.009783 | -3.835e-91 | -22128.5978 |  |  | 0 |  |  | 0 | 0 | 0
-73 | -0.0060833 | 0 | 0.0001 | 3.835e-91 | -0.010029 | -3.835e-91 | -22685.1471 |  |  | 0 |  |  | 0 | 0 | 0
-72 | -0.006 | 0 | 0.0001 | 3.835e-91 | -0.010266 | -3.835e-91 | -23221.9812 |  |  | 0 |  |  | 0 | 0 | 0
-71 | -0.0059167 | 0 | 0.0001 | 3.835e-91 | -0.010495 | -3.835e-91 | -23738.5635 |  |  | 0 |  |  | 0 | 0 | 0
-70 | -0.0058333 | 0 | 0.0001 | 3.835e-91 | -0.010714 | -3.835e-91 | -24234.3772 |  |  | 0 |  |  | 0 | 0 | 0
-69 | -0.00575 | 0 | 0.0001 | 3.835e-91 | -0.010924 | -3.835e-91 | -24708.9259 |  |  | 0 |  |  | 0 | 0 | 0
-68 | -0.0056667 | 0 | 0.0001 | 3.835e-91 | -0.011124 | -3.835e-91 | -25161.7345 |  |  | 0 |  |  | 0 | 0 | 0
-67 | -0.0055833 | 0 | 0.0001 | 3.835e-91 | -0.011314 | -3.835e-91 | -25592.3492 |  |  | 0 |  |  | 0 | 0 | 0
-66 | -0.0055 | 0 | 0.0001 | 3.835e-91 | -0.011495 | -3.835e-91 | -26000.3381 |  |  | 0 |  |  | 0 | 0 | 0
-65 | -0.0054167 | 0 | 0.0001 | 3.835e-91 | -0.011665 | -3.835e-91 | -26385.2916 |  |  | 0 |  |  | 0 | 0 | 0
-64 | -0.0053333 | 0 | 0.0001 | 3.835e-91 | -0.011825 | -3.835e-91 | -26746.8231 |  |  | 0 |  |  | 0 | 0 | 0
-63 | -0.00525 | 0 | 0.0001 | 3.835e-91 | -0.011974 | -3.835e-91 | -27084.5688 |  |  | 0 |  |  | 0 | 0 | 0
-62 | -0.0051667 | 0 | 0.0001 | 3.835e-91 | -0.012113 | -3.835e-91 | -27398.1888 |  |  | 0 |  |  | 0 | 0 | 0
-61 | -0.0050833 | 0 | 0.0001 | 3.835e-91 | -0.012241 | -3.835e-91 | -27687.3665 |  |  | 0 |  |  | 0 | 0 | 0
-60 | -0.005 | 0 | 0.0001 | 3.835e-91 | -0.012357 | -3.835e-91 | -27951.81 |  |  | 0 |  |  | 0 | 0 | 0
-59 | -0.0049167 | 0 | 0.0001 | 3.835e-91 | -0.012463 | -3.835e-91 | -28191.2513 |  |  | 0 |  |  | 0 | 0 | 0
-58 | -0.0048333 | 0 | 0.0001 | 3.835e-91 | -0.012558 | -3.835e-91 | -28405.4476 |  |  | 0 |  |  | 0 | 0 | 0
-57 | -0.00475 | 0 | 0.0001 | 3.835e-91 | -0.012641 | -3.835e-91 | -28594.1805 |  |  | 0 |  |  | 0 | 0 | 0
-56 | -0.0046667 | 0 | 0.0001 | 3.835e-91 | -0.012713 | -3.835e-91 | -28757.2573 |  |  | 0 |  |  | 0 | 0 | 0
-55 | -0.0045833 | 0 | 0.0001 | 3.835e-91 | -0.012774 | -3.835e-91 | -28894.5102 |  |  | 0 |  |  | 0 | 0 | 0
-54 | -0.0045 | 0 | 0.0001 | 3.835e-91 | -0.012823 | -3.835e-91 | -29005.7971 |  |  | 0 |  |  | 0 | 0 | 0
-53 | -0.0044167 | 0 | 0.0001 | 3.835e-91 | -0.012861 | -3.835e-91 | -29091.0015 |  |  | 0 |  |  | 0 | 0 | 0
-52 | -0.0043333 | 0 | 0.0001 | 3.835e-91 | -0.012887 | -3.835e-91 | -29150.0327 |  |  | 0 |  |  | 0 | 0 | 0
-51 | -0.00425 | 0 | 0.0001 | 3.835e-91 | -0.012902 | -3.835e-91 | -29182.8258 |  |  | 0 |  |  | 0 | 0 | 0
-50 | -0.0041667 | 0 | 0.0001 | 3.835e-91 | -0.012905 | -3.835e-91 | -29189.3418 |  |  | 0 |  |  | 0 | 0 | 0
-49 | -0.0040833 | 0 | 0.0001 | 3.835e-91 | -0.012896 | -3.835e-91 | -29169.5677 |  |  | 0 |  |  | 0 | 0 | 0
-48 | -0.004 | 0 | 0.0001 | 3.835e-91 | -0.012875 | -3.835e-91 | -29123.5164 |  |  | 0 |  |  | 0 | 0 | 0
-47 | -0.0039167 | 0 | 0.0001 | 3.835e-91 | -0.012843 | -3.835e-91 | -29051.2268 |  |  | 0 |  |  | 0 | 0 | 0
-46 | -0.0038333 | 0 | 0.0001 | 3.835e-91 | -0.0128 | -3.835e-91 | -28952.7637 |  |  | 0 |  |  | 0 | 0 | 0
-45 | -0.00375 | 0 | 0.0001 | 3.835e-91 | -0.012745 | -3.835e-91 | -28828.2178 |  |  | 0 |  |  | 0 | 0 | 0
-44 | -0.0036667 | 0 | 0.0001 | 3.835e-91 | -0.012678 | -3.835e-91 | -28677.7054 |  |  | 0 |  |  | 0 | 0 | 0
-43 | -0.0035833 | 0 | 0.0001 | 3.835e-91 | -0.0126 | -3.835e-91 | -28501.3686 |  |  | 0 |  |  | 0 | 0 | 0
-42 | -0.0035 | 0 | 0.0001 | 3.835e-91 | -0.012511 | -3.835e-91 | -28299.375 |  |  | 0 |  |  | 0 | 0 | 0
-41 | -0.0034167 | 0 | 0.0001 | 3.835e-91 | -0.012411 | -3.835e-91 | -28071.9173 |  |  | 0 |  |  | 0 | 0 | 0
-40 | -0.0033333 | 0 | 0.0001 | 3.835e-91 | -0.012299 | -3.835e-91 | -27819.2138 |  |  | 0 |  |  | 0 | 0 | 0
-39 | -0.00325 | 0 | 0.0001 | 3.835e-91 | -0.012176 | -3.835e-91 | -27541.5072 |  |  | 0 |  |  | 0 | 0 | 0
-38 | -0.0031667 | 0 | 0.0001 | 3.835e-91 | -0.012042 | -3.835e-91 | -27239.0653 |  |  | 0 |  |  | 0 | 0 | 0
-37 | -0.0030833 | 0 | 0.0001 | 3.835e-91 | -0.011898 | -3.835e-91 | -26912.1802 |  |  | 0 |  |  | 0 | 0 | 0
-36 | -0.003 | 0 | 0.0001 | 3.835e-91 | -0.011743 | -3.835e-91 | -26561.1681 |  |  | 0 |  |  | 0 | 0 | 0
-35 | -0.0029167 | 0 | 0.0001 | 3.835e-91 | -0.011577 | -3.835e-91 | -26186.3689 |  |  | 0 |  |  | 0 | 0 | 0
-34 | -0.0028333 | 0 | 0.0001 | 3.835e-91 | -0.011401 | -3.835e-91 | -25788.1464 |  |  | 0 |  |  | 0 | 0 | 0
-33 | -0.00275 | 0 | 0.0001 | 3.835e-91 | -0.011215 | -3.835e-91 | -25366.887 |  |  | 0 |  |  | 0 | 0 | 0
-32 | -0.0026667 | 0 | 0.0001 | 3.835e-91 | -0.011018 | -3.835e-91 | -24923.0003 |  |  | 0 |  |  | 0 | 0 | 0
-31 | -0.0025833 | 0 | 0.0001 | 3.835e-91 | -0.010812 | -3.835e-91 | -24456.9181 |  |  | 0 |  |  | 0 | 0 | 0
-30 | -0.0025 | 0 | 0.0001 | 3.835e-91 | -0.010597 | -3.835e-91 | -23969.0939 |  |  | 0 |  |  | 0 | 0 | 0
-29 | -0.0024167 | 0 | 0.0001 | 3.835e-91 | -0.010372 | -3.835e-91 | -23460.0031 |  |  | 0 |  |  | 0 | 0 | 0
-28 | -0.0023333 | 0 | 0.0001 | 3.835e-91 | -0.010137 | -3.835e-91 | -22930.1417 |  |  | 0 |  |  | 0 | 0 | 0
-27 | -0.00225 | 0 | 0.0001 | 3.835e-91 | -0.0098941 | -3.835e-91 | -22380.0264 |  |  | 0 |  |  | 0 | 0 | 0
-26 | -0.0021667 | 0 | 0.0001 | 3.835e-91 | -0.0096422 | -3.835e-91 | -21810.1939 |  |  | 0 |  |  | 0 | 0 | 0
-25 | -0.0020833 | 0 | 0.0001 | 3.835e-91 | -0.0093818 | -3.835e-91 | -21221.2004 |  |  | 0 |  |  | 0 | 0 | 0
-24 | -0.002 | 0 | 0.0001 | 3.835e-91 | -0.0091132 | -3.835e-91 | -20613.621 |  |  | 0 |  |  | 0 | 0 | 0
-23 | -0.0019167 | 0 | 0.0001 | 3.835e-91 | -0.0088367 | -3.835e-91 | -19988.0491 |  |  | 0 |  |  | 0 | 0 | 0
-22 | -0.0018333 | 0 | 0.0001 | 3.835e-91 | -0.0085524 | -3.835e-91 | -19345.0959 |  |  | 0 |  |  | 0 | 0 | 0
-21 | -0.00175 | 0 | 0.0001 | 3.835e-91 | -0.0082608 | -3.835e-91 | -18685.3899 |  |  | 0 |  |  | 0 | 0 | 0
-20 | -0.0016667 | 0 | 0.0001 | 3.835e-91 | -0.007962 | -3.835e-91 | -18009.5759 |  |  | 0 |  |  | 0 | 0 | 0
-19 | -0.0015833 | 0 | 0.0001 | 3.835e-91 | -0.0076564 | -3.835e-91 | -17318.3148 |  |  | 0 |  |  | 0 | 0 | 0
-18 | -0.0015 | 0 | 0.0001 | 3.835e-91 | -0.0073442 | -3.835e-91 | -16612.2827 |  |  | 0 |  |  | 0 | 0 | 0
-17 | -0.0014167 | 0 | 0.0001 | 3.835e-91 | -0.0070259 | -3.835e-91 | -15892.1703 |  |  | 0 |  |  | 0 | 0 | 0
-16 | -0.0013333 | 0 | 0.0001 | 3.835e-91 | -0.0067016 | -3.835e-91 | -15158.6822 |  |  | 0 |  |  | 0 | 0 | 0
-15 | -0.00125 | 0 | 0.0001 | 3.835e-91 | -0.0063717 | -3.835e-91 | -14412.5364 |  |  | 0 |  |  | 0 | 0 | 0
-14 | -0.0011667 | 0 | 0.0001 | 3.835e-91 | -0.0060366 | -3.835e-91 | -13654.463 |  |  | 0 |  |  | 0 | 0 | 0
-13 | -0.0010833 | 0 | 0.0001 | 3.835e-91 | -0.0056965 | -3.835e-91 | -12885.2042 |  |  | 0 |  |  | 0 | 0 | 0
-12 | -0.001 | 0 | 0.0001 | 3.835e-91 | -0.0053518 | -3.835e-91 | -12105.5132 |  |  | 0 |  |  | 0 | 0 | 0
-11 | -0.00091667 | 0 | 0.0001 | 3.835e-91 | -0.0050028 | -3.835e-91 | -11316.1535 |  |  | 0 |  |  | 0 | 0 | 0
-10 | -0.00083333 | 0 | 0.0001 | 3.835e-91 | -0.0046499 | -3.835e-91 | -10517.8981 |  |  | 0 |  |  | 0 | 0 | 0
-9 | -0.00075 | 0 | 0.0001 | 3.835e-91 | -0.0042934 | -3.835e-91 | -9711.5289 |  |  | 0 |  |  | 0 | 0 | 0
-8 | -0.00066667 | 0 | 0.0001 | 3.835e-91 | -0.0039337 | -3.835e-91 | -8897.8358 |  |  | 0 |  |  | 0 | 0 | 0
-7 | -0.00058333 | 0 | 0.0001 | 3.835e-91 | -0.0035711 | -3.835e-91 | -8077.6158 |  |  | 0 |  |  | 0 | 0 | 0
-6 | -0.0005 | 0 | 0.0001 | 3.835e-91 | -0.0032059 | -3.835e-91 | -7251.6725 |  |  | 0 |  |  | 0 | 0 | 0
-5 | -0.00041667 | 0 | 0.0001 | 3.835e-91 | -0.0028386 | -3.835e-91 | -6420.8151 |  |  | 0 |  |  | 0 | 0 | 0
-4 | -0.00033333 | 0 | 0.0001 | 3.835e-91 | -0.0024695 | -3.835e-91 | -5585.8578 |  |  | 0 |  |  | 0 | 0 | 0
-3 | -0.00025 | 0 | 0.0001 | 3.835e-91 | -0.0020989 | -3.835e-91 | -4747.6187 |  |  | 0 |  |  | 0 | 0 | 0
-2 | -0.00016667 | 0 | 0.0001 | 3.835e-91 | -0.0017272 | -3.835e-91 | -3906.9191 |  |  | 0 |  |  | 0 | 0 | 0
-1 | -8.3333e-05 | 0 | 0.0001 | 3.835e-91 | -0.0013548 | -3.835e-91 | -3064.583 |  |  | 0 |  |  | 0 | 0 | 0
0 | 0 | 0 | 0.0001 | 3.835e-91 | -0.00098209 | -3.835e-91 | -2221.4359 | 0 | 0 | 0 | 0 | -3.835e-91 | 0 | 90 | 90 | bar: 22 0 to 22 6
1 | 8.3333e-05 | -0.14999 | -0.00088209 | -2.4269e-70 | -0.00065934 | -0.14999 | -1378.3039 | -0.0047112 | -0.14991 | 0.0010606 | -0.0047112 | -0.14991 | 0.0010606 | -91.8 | -91.8
2 | 0.00016667 | -0.22974 | -0.0015414 | -5.225e-65 | -0.00031355 | -0.22974 | -536.0135 | -0.014426 | -0.22929 | 0.0026848 | -0.014426 | -0.22929 | 0.0026848 | -92.8891 | -92.8891
3 | 0.00025 | -0.23937 | -0.001855 | -3.0706e-63 | 5.4878e-05 | -0.23937 | 304.6099 | -0.022527 | -0.23831 | 0.0043764 | -0.022527 | -0.23831 | 0.0043764 | -93.8599 | -93.8599
4 | 0.00033333 | -0.17904 | -0.0018001 | -1.586e-63 | 0.00044552 | -0.17904 | 1142.7425 | -0.02244 | -0.17763 | 0.0056407 | -0.02244 | -0.17763 | 0.0056407 | -94.6092 | -94.6092
5 | 0.00041667 | -0.049003 | -0.0013546 | -3.0441e-66 | 0.00085794 | -0.049003 | 1977.5628 | -0.0076658 | -0.0484 | 0.0059863 | -0.0076658 | -0.0484 | 0.0059863 | -94.8631 | -94.8631
6 | 0.0005 | 0.15044 | -0.00049664 | -7.8825e-76 | 0.0012917 | 0.15044 | 2808.2526 | 0.028189 | 0.14777 | 0.0049294 | 0.028189 | 0.14777 | 0.0049294 | -93.5841 | -93.5841
7 | 0.00058333 | 0.4189 | 0.00079503 | 2.4669e-71 | 0.0017462 | 0.4189 | 3633.998 | 0.091381 | 0.40881 | 0.002057 | 0.091381 | 0.40881 | 0.002057 | -80.5423 | -80.5423
8 | 0.00066667 | 0.75594 | 0.0025412 | 3.1244e-60 | 0.0022211 | 0.75594 | 4453.9896 | 0.188 | 0.73219 | 0.0035626 | 0.188 | 0.73219 | 0.0035626 | 62.0949 | 62.0949
9 | 0.00075 | 1.1611 | 0.0047623 | 3.1316e-54 | 0.0027157 | 1.1611 | 5267.4239 | 0.32392 | 1.115 | 0.011721 | 0.32392 | 1.115 | 0.011721 | 70.2646 | 70.2646
10 | 0.00083333 | 1.6336 | 0.007478 | 6.4136e-50 | 0.0032296 | 1.6336 | 6073.5037 | 0.50482 | 1.5537 | 0.02327 | 0.50482 | 1.5537 | 0.02327 | 71.126 | 71.126
11 | 0.00091667 | 2.1731 | 0.010708 | 1.7261e-46 | 0.0037622 | 2.1731 | 6871.4393 | 0.7361 | 2.0446 | 0.038634 | 0.7361 | 2.0446 | 0.038634 | 70.7577 | 70.7577
12 | 0.001 | 2.7786 | 0.01447 | 1.3001e-43 | 0.0043129 | 2.7786 | 7660.4488 | 1.0229 | 2.5835 | 0.058271 | 1.0229 | 2.5835 | 0.058271 | 69.9629 | 69.9629
13 | 0.0010833 | 3.4495 | 0.018783 | 4.0408e-41 | 0.004881 | 3.4495 | 8439.7591 | 1.37 | 3.1658 | 0.082634 | 1.37 | 3.1658 | 0.082634 | 68.9708 | 68.9708
14 | 0.0011667 | 4.185 | 0.023664 | 6.5105e-39 | 0.0054661 | 4.185 | 9208.6067 | 1.7819 | 3.7867 | 0.11217 | 1.7819 | 3.7867 | 0.11217 | 67.8713 | 67.8713
15 | 0.00125 | 4.984 | 0.02913 | 6.2981e-37 | 0.0060674 | 4.984 | 9966.2384 | 2.2627 | 4.4408 | 0.14731 | 2.2627 | 4.4408 | 0.14731 | 66.7073 | 66.7073
16 | 0.0013333 | 5.8457 | 0.035197 | 4.0454e-35 | 0.0066843 | 5.8457 | 10711.9122 | 2.8162 | 5.1226 | 0.1885 | 2.8162 | 5.1226 | 0.1885 | 65.5014 | 65.5014
17 | 0.0014167 | 6.769 | 0.041882 | 1.8546e-33 | 0.0073161 | 6.769 | 11444.8977 | 3.4457 | 5.8263 | 0.23615 | 3.4457 | 5.8263 | 0.23615 | 64.267 | 64.267
18 | 0.0015 | 7.7528 | 0.049198 | 6.4051e-32 | 0.0079621 | 7.7528 | 12164.477 | 4.1542 | 6.5459 | 0.29067 | 4.1542 | 6.5459 | 0.29067 | 63.0123 | 63.0123
19 | 0.0015833 | 8.796 | 0.05716 | 1.7368e-30 | 0.0086218 | 8.796 | 12869.9455 | 4.9441 | 7.275 | 0.35246 | 4.9441 | 7.275 | 0.35246 | 61.7428 | 61.7428
20 | 0.0016667 | 9.8974 | 0.065782 | 3.8198e-29 | 0.0092942 | 9.8974 | 13560.6125 | 5.8175 | 8.0071 | 0.42191 | 5.8175 | 8.0071 | 0.42191 | 60.4623 | 60.4623
21 | 0.00175 | 11.0557 | 0.075076 | 6.9944e-28 | 0.0099788 | 11.0557 | 14235.802 | 6.7761 | 8.7357 | 0.4994 | 6.7761 | 8.7357 | 0.4994 | 59.1733 | 59.1733
22 | 0.0018333 | 12.2696 | 0.085055 | 1.0892e-26 | 0.010675 | 12.2696 | 14894.853 | 7.8209 | 9.4539 | 0.5853 | 7.8209 | 9.4539 | 0.5853 | 57.8778 | 57.8778
23 | 0.0019167 | 13.5377 | 0.095729 | 1.4681e-25 | 0.011381 | 13.5377 | 15537.1207 | 8.9526 | 10.1548 | 0.67994 | 8.9526 | 10.1548 | 0.67994 | 56.5772 | 56.5772
24 | 0.002 | 14.8586 | 0.10711 | 1.7382e-24 | 0.012098 | 14.8586 | 16161.9765 | 10.1714 | 10.8314 | 0.78369 | 10.1714 | 10.8314 | 0.78369 | 55.2726 | 55.2726
25 | 0.0020833 | 16.2308 | 0.11921 | 1.8304e-23 | 0.012824 | 16.2308 | 16768.8094 | 11.4769 | 11.4769 | 0.89685 | 11.4769 | 11.4769 | 0.89685 | 53.965 | 53.965
26 | 0.0021667 | 17.6529 | 0.13203 | 1.7328e-22 | 0.013558 | 17.6529 | 17357.0258 | 12.8684 | 12.0842 | 1.0197 | 12.8684 | 12.0842 | 1.0197 | 52.6549 | 52.6549
27 | 0.00225 | 19.1231 | 0.14559 | 1.4883e-21 | 0.014299 | 19.1231 | 17926.0506 | 14.3445 | 12.6464 | 1.1527 | 14.3445 | 12.6464 | 1.1527 | 51.3429 | 51.3429
28 | 0.0023333 | 20.64 | 0.15989 | 1.169e-20 | 0.015048 | 20.64 | 18475.3278 | 15.9034 | 13.1564 | 1.2959 | 15.9034 | 13.1564 | 1.2959 | 50.0295 | 50.0295
29 | 0.0024167 | 22.2018 | 0.17494 | 8.4566e-20 | 0.015802 | 22.2018 | 19004.3205 | 17.5429 | 13.6076 | 1.4497 | 17.5429 | 13.6076 | 1.4497 | 48.7151 | 48.7151
30 | 0.0025 | 23.8068 | 0.19074 | 5.6687e-19 | 0.016562 | 23.8068 | 19512.5122 | 19.2601 | 13.9933 | 1.6143 | 19.2601 | 13.9933 | 1.6143 | 47.3999 | 47.3999
31 | 0.0025833 | 25.4533 | 0.2073 | 3.5403e-18 | 0.017326 | 25.4533 | 19999.4066 | 21.0519 | 14.3069 | 1.79 | 21.0519 | 14.3069 | 1.79 | 46.0843 | 46.0843
32 | 0.0026667 | 27.1394 | 0.22463 | 2.07e-17 | 0.018094 | 27.1394 | 20464.5286 | 22.9146 | 14.542 | 1.977 | 22.9146 | 14.542 | 1.977 | 44.7685 | 44.7685
33 | 0.00275 | 28.8634 | 0.24272 | 1.1381e-16 | 0.018864 | 28.8634 | 20907.4244 | 24.844 | 14.6927 | 2.1755 | 24.844 | 14.6927 | 2.1755 | 43.4527 | 43.4527
34 | 0.0028333 | 30.6234 | 0.26159 | 5.9059e-16 | 0.019637 | 30.6234 | 21327.6623 | 26.8355 | 14.7529 | 2.3856 | 26.8355 | 14.7529 | 2.3856 | 42.137 | 42.137
35 | 0.0029167 | 32.4174 | 0.28122 | 2.9032e-15 | 0.02041 | 32.4174 | 21724.8329 | 28.8841 | 14.7172 | 2.6076 | 28.8841 | 14.7172 | 2.6076 | 40.8216 | 40.8216
36 | 0.003 | 34.2435 | 0.30163 | 1.3561e-14 | 0.021184 | 34.2435 | 22098.5495 | 30.9845 | 14.5802 | 2.8415 | 30.9845 | 14.5802 | 2.8415 | 39.5068 | 39.5068
37 | 0.0030833 | 36.0998 | 0.32282 | 6.0369e-14 | 0.021958 | 36.0998 | 22448.4485 | 33.1308 | 14.337 | 3.0876 | 33.1308 | 14.337 | 3.0876 | 38.1925 | 38.1925
38 | 0.0031667 | 37.9843 | 0.34478 | 2.5677e-13 | 0.02273 | 37.9843 | 22774.1899 | 35.3169 | 13.9829 | 3.3459 | 35.3169 | 13.9829 | 3.3459 | 36.8789 | 36.8789
39 | 0.00325 | 39.8948 | 0.3675 | 1.046e-12 | 0.0235 | 39.8948 | 23075.4574 | 37.5363 | 13.5139 | 3.6165 | 37.5363 | 13.5139 | 3.6165 | 35.5662 | 35.5662
40 | 0.0033333 | 41.8295 | 0.391 | 4.0904e-12 | 0.024267 | 41.8295 | 23351.959 | 39.7822 | 12.926 | 3.8995 | 39.7822 | 12.926 | 3.8995 | 34.2545 | 34.2545
41 | 0.0034167 | 43.7861 | 0.41527 | 1.5384e-11 | 0.02503 | 43.7861 | 23603.427 | 42.0476 | 12.2159 | 4.1949 | 42.0476 | 12.2159 | 4.1949 | 32.9438 | 32.9438
42 | 0.0035 | 45.7627 | 0.4403 | 5.5755e-11 | 0.025789 | 45.7627 | 23829.6184 | 44.325 | 11.3807 | 4.5029 | 44.325 | 11.3807 | 4.5029 | 31.6342 | 31.6342
43 | 0.0035833 | 47.757 | 0.46609 | 1.9504e-10 | 0.026543 | 47.757 | 24030.3152 | 46.6069 | 10.4179 | 4.8234 | 46.6069 | 10.4179 | 4.8234 | 30.3258 | 30.3258
44 | 0.0036667 | 49.767 | 0.49263 | 6.5963e-10 | 0.02729 | 49.767 | 24205.3245 | 48.8855 | 9.3254 | 5.1564 | 48.8855 | 9.3254 | 5.1564 | 29.0188 | 29.0188
45 | 0.00375 | 51.7905 | 0.51992 | 2.16e-09 | 0.028031 | 51.7905 | 24354.4788 | 51.1529 | 8.1018 | 5.5019 | 51.1529 | 8.1018 | 5.5019 | 27.7132 | 27.7132
46 | 0.0038333 | 53.8254 | 0.54795 | 6.8572e-09 | 0.028763 | 53.8254 | 24477.6359 | 53.401 | 6.7461 | 5.8599 | 53.401 | 6.7461 | 5.8599 | 26.409 | 26.409
47 | 0.0039167 | 55.8694 | 0.57672 | 2.1133e-08 | 0.029488 | 55.8694 | 24574.6795 | 55.6215 | 5.2578 | 6.2303 | 55.6215 | 5.2578 | 6.2303 | 25.1064 | 25.1064
48 | 0.004 | 57.9204 | 0.60621 | 6.33e-08 | 0.030203 | 57.9204 | 24645.519 | 57.8062 | 3.6369 | 6.6131 | 57.8062 | 3.6369 | 6.6131 | 23.8054 | 23.8054
49 | 0.0040833 | 59.9763 | 0.63641 | 1.8448e-07 | 0.030908 | 59.9763 | 24690.0894 | 59.9467 | 1.8839 | 7.0081 | 59.9467 | 1.8839 | 7.0081 | 22.5061 | 22.5061
50 | 0.0041667 | 62.0347 | 0.66732 | 5.2366e-07 | 0.031602 | 62.0347 | 24708.352 | 62.0347 | 1.7573e-14 | 7.4152 | 62.0347 | 1.7573e-14 | 7.4152 | 21.2086 | 21.2086
51 | 0.00425 | 64.0936 | 0.69892 | 1.4492e-06 | 0.032284 | 64.0936 | 24700.2937 | 64.062 | -2.0132 | 7.8344 | 64.062 | -2.0132 | 7.8344 | 19.913 | 19.913
52 | 0.0043333 | 66.1507 | 0.7312 | 3.9137e-06 | 0.032955 | 66.1507 | 24665.9277 | 66.0202 | -4.1536 | 8.2654 | 66.0202 | -4.1536 | 8.2654 | 18.6192 | 18.6192
53 | 0.0044167 | 68.2039 | 0.76416 | 1.0322e-05 | 0.033612 | 68.2039 | 24605.2927 | 67.9012 | -6.4186 | 8.7081 | 67.9012 | -6.4185 | 8.7081 | 17.3275 | 17.3275
54 | 0.0045 | 70.2509 | 0.79777 | 2.6611e-05 | 0.034256 | 70.2508 | 24518.4539 | 69.6969 | -8.8048 | 9.1624 | 69.6969 | -8.8048 | 9.1624 | 16.0379 | 16.0379
55 | 0.0045833 | 72.2895 | 0.83203 | 6.7107e-05 | 0.034886 | 72.2895 | 24405.5017 | 71.3995 | -11.3086 | 9.6279 | 71.3995 | -11.3086 | 9.6279 | 14.7503 | 14.7503
56 | 0.0046667 | 74.3177 | 0.86691 | 0.00016566 | 0.0355 | 74.3176 | 24266.5529 | 73.0014 | -13.9258 | 10.1046 | 73.0012 | -13.9257 | 10.1046 | 13.4651 | 13.4651
57 | 0.00475 | 76.3333 | 0.90241 | 0.00040055 | 0.036098 | 76.3329 | 24101.7493 | 74.4949 | -16.6516 | 10.5921 | 74.4945 | -16.6515 | 10.5921 | 12.1821 | 12.1821
58 | 0.0048333 | 78.334 | 0.93851 | 0.00094931 | 0.036678 | 78.333 | 23911.2588 | 75.873 | -19.4809 | 11.0902 | 75.872 | -19.4806 | 11.0902 | 10.9014 | 10.9014
59 | 0.0049167 | 80.3178 | 0.97519 | 0.0022064 | 0.037238 | 80.3156 | 23695.2742 | 77.1286 | -22.4079 | 11.5987 | 77.1265 | -22.4073 | 11.5987 | 9.6232 | 9.6233
60 | 0.005 | 82.2825 | 1.0124 | 0.005032 | 0.037773 | 82.2775 | 23454.0137 | 78.2553 | -25.4267 | 12.1172 | 78.2505 | -25.4251 | 12.1172 | 8.3475 | 8.3477
61 | 0.0050833 | 84.2261 | 1.0502 | 0.011265 | 0.038275 | 84.2148 | 23187.7203 | 79.2467 | -28.5306 | 12.6455 | 79.2361 | -28.5267 | 12.6453 | 7.0744 | 7.0747
62 | 0.0051667 | 86.1464 | 1.0885 | 0.02476 | 0.038727 | 86.1217 | 22896.6617 | 80.0969 | -31.7126 | 13.1832 | 80.0739 | -31.7035 | 13.1829 | 5.804 | 5.8046
63 | 0.00525 | 88.0415 | 1.1272 | 0.053429 | 0.039096 | 87.9881 | 22581.13 | 80.8005 | -34.9655 | 13.7299 | 80.7515 | -34.9443 | 13.7293 | 4.5363 | 4.5376
64 | 0.0053333 | 89.9093 | 1.1663 | 0.11312 | 0.03932 | 89.7961 | 22241.4417 | 81.3523 | -38.2815 | 14.2855 | 81.25 | -38.2333 | 14.2841 | 3.2714 | 3.2742
65 | 0.0054167 | 91.7477 | 1.2056 | 0.23461 | 0.039284 | 91.5131 | 21877.9368 | 81.7478 | -41.6526 | 14.8494 | 81.5388 | -41.5461 | 14.8466 | 2.0095 | 2.0151
66 | 0.0055 | 93.5549 | 1.2449 | 0.47502 | 0.0388 | 93.0799 | 21490.9789 | 81.9828 | -45.0704 | 15.4213 | 81.5666 | -44.8416 | 15.4155 | 0.75051 | 0.76183
67 | 0.0055833 | 95.3289 | 1.2837 | 0.93315 | 0.037595 | 94.3958 | 21080.9548 | 82.0536 | -48.5264 | 16.0008 | 81.2504 | -48.0514 | 15.9892 | -0.5054 | -0.48308
68 | 0.0056667 | 97.0678 | 1.3213 | 1.761 | 0.035392 | 95.3068 | 20648.274 | 81.9571 | -52.0115 | 16.5875 | 80.4702 | -51.0679 | 16.5651 | -1.7582 | -1.7155
69 | 0.00575 | 98.7697 | 1.3567 | 3.15 | 0.032101 | 95.6197 | 20193.3683 | 81.6905 | -55.5168 | 17.181 | 79.0852 | -53.7462 | 17.1393 | -3.0077 | -2.9296
70 | 0.0058333 | 100.4328 | 1.3888 | 5.2693 | 0.028027 | 95.1634 | 19716.6916 | 81.2518 | -59.0329 | 17.7808 | 76.9888 | -55.9357 | 17.707 | -4.2539 | -4.1178
71 | 0.0059167 | 102.0552 | 1.4168 | 8.1781 | 0.023773 | 93.8772 | 19218.7189 | 80.6394 | -62.5504 | 18.3866 | 74.1775 | -57.538 | 18.2631 | -5.4967 | -5.2728
72 | 0.006 | 103.6353 | 1.4406 | 11.7934 | 0.019883 | 91.8419 | 18699.9466 | 79.8524 | -66.0596 | 18.9978 | 70.7654 | -58.5423 | 18.803 | -6.7359 | -6.3888
73 | 0.0060833 | 105.1713 | 1.4605 | 15.9444 | 0.016609 | 89.2269 | 18160.8915 | 78.8902 | -69.551 | 19.6141 | 66.9301 | -59.0068 | 19.3231 | -7.9716 | -7.4622
74 | 0.0061667 | 106.6616 | 1.4771 | 20.4479 | 0.013962 | 86.2136 | 17602.0902 | 77.7529 | -73.0149 | 20.2348 | 62.847 | -59.0173 | 19.8211 | -9.2036 | -8.4915
75 | 0.00625 | 108.1045 | 1.491 | 25.1499 | 0.01185 | 82.9546 | 17024.0991 | 76.4414 | -76.4414 | 20.8596 | 58.6577 | -58.6577 | 20.2956 | -10.4318 | -9.4768
76 | 0.0063333 | 109.4984 | 1.5029 | 29.9342 | 0.010162 | 79.5642 | 16427.4933 | 74.9568 | -79.8209 | 21.488 | 54.4654 | -57.9998 | 20.7458 | -11.6561 | -10.4189
77 | 0.0064167 | 110.8419 | 1.5131 | 34.7178 | 0.0087996 | 76.1241 | 15812.8664 | 73.301 | -83.1437 | 22.1194 | 50.3418 | -57.1015 | 21.1716 | -12.8764 | -11.3194
78 | 0.0065 | 112.1334 | 1.5219 | 39.4419 | 0.0076877 | 72.6915 | 15180.8295 | 71.4765 | -86.4003 | 22.7534 | 46.3353 | -56.0097 | 21.573 | -14.0926 | -12.1801
79 | 0.0065833 | 113.3715 | 1.5295 | 44.0658 | 0.0067683 | 69.3058 | 14532.0112 | 69.4862 | -89.5811 | 23.3894 | 42.478 | -54.7623 | 21.9506 | -15.3046 | -13.0027
80 | 0.0066667 | 114.5549 | 1.5363 | 48.5609 | 0.0059986 | 65.994 | 13867.0565 | 67.3337 | -92.6769 | 24.027 | 38.7903 | -53.3903 | 22.3049 | -16.5123 | -13.7891
81 | 0.00675 | 115.6823 | 1.5423 | 52.9079 | 0.0053469 | 62.7744 | 13186.6263 | 65.0231 | -95.6786 | 24.6655 | 35.2845 | -51.9195 | 22.6366 | -17.7156 | -14.541
82 | 0.0068333 | 116.7523 | 1.5477 | 57.0935 | 0.004789 | 59.6588 | 12491.3968 | 62.559 | -98.5772 | 25.3046 | 31.9668 | -50.3716 | 22.9467 | -18.9143 | -15.2602
83 | 0.0069167 | 117.7638 | 1.5524 | 61.1091 | 0.0043069 | 56.6547 | 11782.0588 | 59.9467 | -101.3642 | 25.9435 | 28.8396 | -48.7651 | 23.2358 | -20.1084 | -15.9482
84 | 0.007 | 118.7156 | 1.5567 | 64.9495 | 0.0038865 | 53.7661 | 11059.3169 | 57.1917 | -104.0313 | 26.5819 | 25.902 | -47.1156 | 23.505 | -21.2978 | -16.6064
85 | 0.0070833 | 119.6067 | 1.5606 | 68.6119 | 0.0035168 | 50.9948 | 10323.8891 | 54.3003 | -106.5703 | 27.2192 | 23.1512 | -45.4367 | 23.7552 | -22.4822 | -17.2361
86 | 0.0071667 | 120.4359 | 1.5642 | 72.0951 | 0.0031895 | 48.3409 | 9576.5057 | 51.2791 | -108.9737 | 27.8548 | 20.5825 | -43.7401 | 23.9871 | -23.6616 | -17.8387
87 | 0.00725 | 121.2024 | 1.5673 | 75.3995 | 0.0028975 | 45.803 | 8817.909 | 48.1353 | -111.2341 | 28.4882 | 18.1906 | -42.0359 | 24.2019 | -24.8359 | -18.4153
88 | 0.0073333 | 121.9053 | 1.5702 | 78.5263 | 0.0026355 | 43.379 | 8048.8523 | 44.8763 | -113.3447 | 29.1189 | 15.9689 | -40.3328 | 24.4002 | -26.0049 | -18.967
89 | 0.0074167 | 122.5436 | 1.5729 | 81.4775 | 0.0023989 | 41.0661 | 7270.099 | 41.5102 | -115.299 | 29.7463 | 13.9107 | -38.6383 | 24.5831 | -27.1685 | -19.4947
90 | 0.0075 | 123.1167 | 1.5753 | 84.2556 | 0.0021842 | 38.8611 | 6482.4223 | 38.0452 | -117.091 | 30.3699 | 12.0087 | -36.9591 | 24.7513 | -28.3265 | -19.9994
91 | 0.0075833 | 123.6238 | 1.5775 | 86.8636 | 0.0019884 | 36.7602 | 5686.6042 | 34.4899 | -118.7152 | 30.9891 | 10.2558 | -35.3006 | 24.9057 | -29.4788 | -20.4819
92 | 0.0076667 | 124.0643 | 1.5794 | 89.3046 | 0.0018088 | 34.7597 | 4883.4345 | 30.8535 | -120.1666 | 31.6035 | 8.6444 | -33.6677 | 25.0471 | -30.6253 | -20.9432
93 | 0.00775 | 124.4375 | 1.5813 | 91.5818 | 0.0016435 | 32.8557 | 4073.7104 | 27.1452 | -121.4407 | 32.2125 | 7.1673 | -32.0644 | 25.1762 | -31.7658 | -21.3838
94 | 0.0078333 | 124.7431 | 1.5829 | 93.6989 | 0.0014906 | 31.0442 | 3258.2356 | 23.3745 | -122.5335 | 32.8156 | 5.8171 | -30.4943 | 25.2938 | -32.9001 | -21.8047
95 | 0.0079167 | 124.9804 | 1.5844 | 95.6594 | 0.0013486 | 29.3211 | 2437.8194 | 19.5512 | -123.4417 | 33.4123 | 4.5868 | -28.9601 | 25.4006 | -34.0282 | -22.2064
96 | 0.008 | 125.1493 | 1.5857 | 97.4667 | 0.0012162 | 27.6826 | 1613.2759 | 15.6854 | -124.1624 | 34.002 | 3.4695 | -27.4643 | 25.4973 | -35.1498 | -22.5896
97 | 0.0080833 | 125.2492 | 1.587 | 99.1246 | 0.0010923 | 26.1247 | 785.4233 | 11.787 | -124.6934 | 34.5843 | 2.4585 | -26.0087 | 25.5845 | -36.2647 | -22.9549
98 | 0.0081667 | 125.2801 | 1.588 | 100.6365 | 0.00097599 | 24.6436 | -44.9168 | 7.8664 | -125.0329 | 35.1587 | 1.5474 | -24.595 | 25.6629 | -37.3729 | -23.3029
99 | 0.00825 | 125.2417 | 1.589 | 102.006 | 0.00086638 | 23.2357 | -876.9205 | 3.9339 | -125.1799 | 35.7247 | 0.72985 | -23.2243 | 25.733 | -38.474 | -23.6342
100 | 0.0083333 | 125.1339 | 1.5899 | 103.2366 | 0.00076274 | 21.8974 | -1709.7624 | 7.0895e-14 | -125.1339 | 36.2818 | 1.2406e-14 | -21.8974 | 25.7955 | -39.568 | -23.9492
101 | 0.0084167 | 124.9567 | 1.5907 | 104.3317 | 0.00066444 | 20.6251 | -2542.6159 | -3.925 | -124.8951 | 36.8296 | -0.64785 | -20.6149 | 25.8508 | -40.6547 | -24.2486
102 | 0.0085 | 124.7102 | 1.5913 | 105.2947 | 0.00057091 | 19.4155 | -3374.6548 | -7.8306 | -124.4641 | 37.3676 | -1.2191 | -19.3772 | 25.8996 | -41.7338 | -24.5328
103 | 0.0085833 | 124.3943 | 1.5919 | 106.1289 | 0.00048165 | 18.2655 | -4205.0535 | -11.7065 | -123.8423 | 37.8954 | -1.7189 | -18.1844 | 25.9422 | -42.8053 | -24.8023
104 | 0.0086667 | 124.0094 | 1.5924 | 106.8376 | 0.00039622 | 17.1718 | -5032.9881 | -15.5425 | -123.0316 | 38.4125 | -2.1522 | -17.0364 | 25.9792 | -43.8687 | -25.0576
105 | 0.00875 | 123.5556 | 1.5928 | 107.4239 | 0.00031421 | 16.1317 | -5857.6371 | -19.3284 | -122.0344 | 38.9186 | -2.5235 | -15.933 | 26.0109 | -44.9241 | -25.2991
106 | 0.0088333 | 123.0332 | 1.5931 | 107.8911 | 0.00023527 | 15.1421 | -6678.1822 | -23.0541 | -120.854 | 39.4133 | -2.8373 | -14.8739 | 26.0379 | -45.9711 | -25.5272
107 | 0.0089167 | 122.4427 | 1.5933 | 108.2422 | 0.00015909 | 14.2005 | -7493.8093 | -26.71 | -119.4939 | 39.8961 | -3.0977 | -13.8585 | 26.0606 | -47.0096 | -25.7423
108 | 0.009 | 121.7844 | 1.5935 | 108.4802 | 8.537e-05 | 13.3042 | -8303.7092 | -30.2866 | -117.9584 | 40.3667 | -3.3086 | -12.8862 | 26.0793 | -48.0392 | -25.945
109 | 0.0090833 | 121.0589 | 1.5936 | 108.6082 | 1.3852e-05 | 12.4508 | -9107.0781 | -33.7744 | -116.2521 | 40.8247 | -3.4737 | -11.9564 | 26.0943 | -49.0599 | -26.1355
110 | 0.0091667 | 120.2668 | 1.5936 | 108.6289 | -5.5701e-05 | 11.6378 | -9903.119 | -37.1645 | -114.3805 | 41.2699 | -3.5963 | -11.0683 | 26.1061 | -50.0713 | -26.3143
111 | 0.00925 | 119.4086 | 1.5935 | 108.5454 | -0.00012351 | 10.8632 | -10691.0418 | -40.4482 | -112.3493 | 41.7019 | -3.6798 | -10.221 | 26.1149 | -51.0733 | -26.4817
112 | 0.0093333 | 118.4852 | 1.5934 | 108.3605 | -0.00018977 | 10.1247 | -11470.0646 | -43.6173 | -110.1648 | 42.1204 | -3.7271 | -9.4137 | 26.1211 | -52.0655 | -26.6382
113 | 0.0094167 | 117.4972 | 1.5932 | 108.0769 | -0.00025466 | 9.4203 | -12239.4144 | -46.6638 | -107.8336 | 42.5252 | -3.7412 | -8.6455 | 26.1249 | -53.0478 | -26.7841
114 | 0.0095 | 116.4456 | 1.5929 | 107.6975 | -0.00031836 | 8.7481 | -12998.3275 | -49.5801 | -105.3631 | 42.916 | -3.7247 | -7.9155 | 26.1267 | -54.0198 | -26.9197
115 | 0.0095833 | 115.3312 | 1.5926 | 107.225 | -0.00038102 | 8.1062 | -13746.0508 | -52.3593 | -102.7608 | 43.2926 | -3.6801 | -7.2226 | 26.1267 | -54.9813 | -27.0454
116 | 0.0096667 | 114.1549 | 1.5923 | 106.6621 | -0.00044279 | 7.4929 | -14481.842 | -54.9945 | -100.0347 | 43.6548 | -3.6097 | -6.566 | 26.1251 | -55.9321 | -27.1615
117 | 0.00975 | 112.9179 | 1.5918 | 106.0114 | -0.00050381 | 6.9065 | -15204.9707 | -57.4799 | -97.1932 | 44.0023 | -3.5157 | -5.9447 | 26.1223 | -56.8719 | -27.2684
118 | 0.0098333 | 111.6211 | 1.5913 | 105.2757 | -0.00056421 | 6.3455 | -15914.719 | -59.8096 | -94.2448 | 44.3351 | -3.4001 | -5.3576 | 26.1183 | -57.8003 | -27.3665
119 | 0.0099167 | 110.2658 | 1.5907 | 104.4575 | -0.0006241 | 5.8083 | -16610.3823 | -61.9786 | -91.1987 | 44.653 | -3.2647 | -4.8039 | 26.1134 | -58.7171 | -27.4559
120 | 0.01 | 108.8531 | 1.5901 | 103.5596 | -0.00068361 | 5.2935 | -17291.2697 | -63.9823 | -88.064 | 44.9558 | -3.1114 | -4.2825 | 26.1079 | -59.622 | -27.5372
121 | 0.010083 | 107.3844 | 1.5894 | 102.5846 | -0.00074285 | 4.7998 | -17956.7051 | -65.8166 | -84.8503 | 45.2436 | -2.9418 | -3.7926 | 26.1019 | -60.5147 | -27.6105
122 | 0.010167 | 105.8608 | 1.5887 | 101.5349 | -0.00080192 | 4.3259 | -18606.0275 | -67.4782 | -81.5671 | 45.5162 | -2.7574 | -3.3331 | 26.0955 | -61.395 | -27.6762
123 | 0.01025 | 104.2838 | 1.5879 | 100.4133 | -0.00086093 | 3.8705 | -19238.592 | -68.9641 | -78.2244 | 45.7736 | -2.5596 | -2.9033 | 26.089 | -62.2624 | -27.7346
124 | 0.010333 | 102.6549 | 1.587 | 99.2224 | -0.00091998 | 3.4325 | -19853.7701 | -70.2721 | -74.8322 | 46.0158 | -2.3497 | -2.5021 | 26.0826 | -63.1167 | -27.786
125 | 0.010417 | 100.9754 | 1.5861 | 97.9647 | -0.00097917 | 3.0107 | -20450.9505 | -71.4004 | -71.4004 | 46.2428 | -2.1289 | -2.1289 | 26.0763 | -63.9575 | -27.8306
126 | 0.0105 | 99.2469 | 1.5851 | 96.6427 | -0.0010386 | 2.6041 | -21029.5397 | -72.3479 | -67.9392 | 46.4546 | -1.8983 | -1.7826 | 26.0703 | -64.7846 | -27.8689
127 | 0.010583 | 97.471 | 1.5841 | 95.2592 | -0.0010983 | 2.2117 | -21588.9626 | -73.1141 | -64.4587 | 46.6514 | -1.6591 | -1.4627 | 26.0648 | -65.5976 | -27.9011
128 | 0.010667 | 95.6493 | 1.583 | 93.8167 | -0.0011585 | 1.8326 | -22128.6628 | -73.699 | -60.9691 | 46.8333 | -1.412 | -1.1681 | 26.0598 | -66.3961 | -27.9274
129 | 0.01075 | 93.7834 | 1.5818 | 92.3177 | -0.0012192 | 1.4657 | -22648.1036 | -74.1034 | -57.4805 | 47.0003 | -1.1582 | -0.89836 | 26.0556 | -67.1798 | -27.9482
130 | 0.010833 | 91.8752 | 1.5806 | 90.7649 | -0.0012806 | 1.1103 | -23146.7684 | -74.3286 | -54.0029 | 47.1527 | -0.89824 | -0.65261 | 26.0521 | -67.9485 | -27.9637
131 | 0.010917 | 89.9262 | 1.5793 | 89.1608 | -0.0013426 | 0.76542 | -23624.1607 | -74.3762 | -50.546 | 47.2906 | -0.63306 | -0.43023 | 26.0496 | -68.7016 | -27.9742
132 | 0.011 | 87.9384 | 1.578 | 87.5081 | -0.0014055 | 0.43031 | -24079.8055 | -74.2488 | -47.1198 | 47.4142 | -0.36333 | -0.23057 | 26.0481 | -69.439 | -27.98
133 | 0.011083 | 85.9135 | 1.5766 | 85.8093 | -0.0014692 | 0.1042 | -24513.249 | -73.9494 | -43.7335 | 47.5239 | -0.089687 | -0.053041 | 26.0477 | -70.1602 | -27.9814
134 | 0.011167 | 83.8535 | 1.5751 | 84.0672 | -0.0015341 | -0.21368 | -24924.0592 | -73.4814 | -40.3967 | 47.6199 | 0.18725 | 0.10294 | 26.0485 | -70.865 | -27.9786
135 | 0.01125 | 81.7602 | 1.5736 | 82.2842 | -0.0016 | -0.52404 | -25311.8268 | -72.8488 | -37.1183 | 47.7024 | 0.46692 | 0.23791 | 26.0507 | -71.5528 | -27.9719
136 | 0.011333 | 79.6355 | 1.572 | 80.4631 | -0.0016672 | -0.82757 | -25676.1649 | -72.0564 | -33.9071 | 47.7719 | 0.74881 | 0.35236 | 26.0542 | -72.2236 | -27.9616
137 | 0.011417 | 77.4815 | 1.5703 | 78.6064 | -0.0017358 | -1.1249 | -26016.71 | -71.109 | -30.7716 | 47.8287 | 1.0324 | 0.44677 | 26.0591 | -72.8767 | -27.948
138 | 0.0115 | 75.3001 | 1.5686 | 76.7169 | -0.0018058 | -1.4168 | -26333.1219 | -70.0122 | -27.7198 | 47.8732 | 1.3173 | 0.52157 | 26.0656 | -73.5121 | -27.9312
139 | 0.011583 | 73.0933 | 1.5668 | 74.7971 | -0.0018775 | -1.7038 | -26625.0843 | -68.7721 | -24.7595 | 47.9058 | 1.6031 | 0.57716 | 26.0737 | -74.1292 | -27.9116
140 | 0.011667 | 70.8632 | 1.5649 | 72.8498 | -0.001951 | -1.9866 | -26892.3052 | -67.3949 | -21.8979 | 47.9271 | 1.8894 | 0.6139 | 26.0835 | -74.7278 | -27.8895
141 | 0.01175 | 68.6119 | 1.5629 | 70.8777 | -0.0020263 | -2.2657 | -27134.5167 | -65.8876 | -19.1421 | 47.9374 | 2.1758 | 0.63212 | 26.095 | -75.3076 | -27.865
142 | 0.011833 | 66.3415 | 1.5609 | 68.8833 | -0.0021038 | -2.5418 | -27351.4758 | -64.2573 | -16.4985 | 47.9373 | 2.462 | 0.63213 | 26.1083 | -75.8683 | -27.8385
143 | 0.011917 | 64.0541 | 1.5588 | 66.8695 | -0.0021834 | -2.8155 | -27542.9645 | -62.5114 | -13.973 | 47.9273 | 2.7477 | 0.61418 | 26.1235 | -76.4096 | -27.8101
144 | 0.012 | 61.7517 | 1.5566 | 64.839 | -0.0022655 | -3.0873 | -27708.7897 | -60.6579 | -11.5711 | 47.908 | 3.0326 | 0.57849 | 26.1405 | -76.9312 | -27.7803
145 | 0.012083 | 59.4366 | 1.5544 | 62.7944 | -0.0023501 | -3.3577 | -27848.7839 | -58.7049 | -9.2979 | 47.88 | 3.3164 | 0.52527 | 26.1596 | -77.4329 | -27.7491
146 | 0.012167 | 57.111 | 1.552 | 60.7385 | -0.0024376 | -3.6275 | -27962.805 | -56.6606 | -7.1579 | 47.844 | 3.5989 | 0.45465 | 26.1806 | -77.9144 | -27.717
147 | 0.01225 | 54.7769 | 1.5496 | 58.6741 | -0.002528 | -3.8971 | -28050.7364 | -54.5338 | -5.155 | 47.8004 | 3.8799 | 0.36675 | 26.2037 | -78.3755 | -27.6841
148 | 0.012333 | 52.4366 | 1.547 | 56.6038 | -0.0026217 | -4.1672 | -28112.4874 | -52.3331 | -3.2925 | 47.7501 | 4.159 | 0.26166 | 26.2289 | -78.816 | -27.6506
149 | 0.012417 | 50.0922 | 1.5444 | 54.5306 | -0.002719 | -4.4384 | -28147.9932 | -50.0675 | -1.5734 | 47.6936 | 4.4362 | 0.13941 | 26.2562 | -79.2359 | -27.617
150 | 0.0125 | 47.746 | 1.5417 | 52.4572 | -0.00282 | -4.7112 | -28157.2149 | -47.746 | -5.1178e-14 | 47.6317 | 4.7112 | 5.0498e-15 | 26.2857 | -79.6348 | -27.5833
151 | 0.012583 | 45.4001 | 1.5389 | 50.3863 | -0.002925 | -4.9862 | -28140.1393 | -45.3777 | 1.4261 | 47.5651 | 4.9838 | -0.15662 | 26.3175 | -80.0129 | -27.5499
152 | 0.012667 | 43.0567 | 1.536 | 48.3209 | -0.0030344 | -5.2642 | -28096.7795 | -42.9717 | 2.7036 | 47.4945 | 5.2538 | -0.33054 | 26.3515 | -80.3699 | -27.5171
153 | 0.01275 | 40.718 | 1.5329 | 46.2637 | -0.0031486 | -5.5457 | -28027.1744 | -40.5373 | 3.8319 | 47.4206 | 5.5211 | -0.5219 | 26.3878 | -80.7059 | -27.485
154 | 0.012833 | 38.3862 | 1.5298 | 44.2176 | -0.0032679 | -5.8314 | -27931.3888 | -38.0835 | 4.8111 | 47.3443 | 5.7854 | -0.73087 | 26.4265 | -81.0208 | -27.454
155 | 0.012917 | 36.0635 | 1.5265 | 42.1856 | -0.0033926 | -6.122 | -27809.5133 | -35.6195 | 5.6416 | 47.2662 | 6.0467 | -0.9577 | 26.4676 | -81.3149 | -27.4243
156 | 0.013 | 33.752 | 1.5231 | 40.1704 | -0.0035233 | -6.4183 | -27661.6644 | -33.1542 | 6.3245 | 47.1871 | 6.3046 | -1.2027 | 26.5111 | -81.5881 | -27.3963
157 | 0.013083 | 31.4539 | 1.5196 | 38.175 | -0.0036603 | -6.721 | -27487.9841 | -30.6964 | 6.8615 | 47.1078 | 6.5592 | -1.4661 | 26.557 | -81.8406 | -27.3701
158 | 0.013167 | 29.1714 | 1.5159 | 36.2023 | -0.0038043 | -7.0309 | -27288.64 | -28.2549 | 7.2546 | 47.0291 | 6.81 | -1.7485 | 26.6055 | -82.0727 | -27.3461
159 | 0.01325 | 26.9065 | 1.5121 | 34.2554 | -0.0039557 | -7.3488 | -27063.8251 | -25.8382 | 7.5067 | 46.9516 | 7.057 | -2.0503 | 26.6565 | -82.2845 | -27.3245
160 | 0.013333 | 24.6615 | 1.5082 | 32.3372 | -0.004115 | -7.6757 | -26813.7572 | -23.4545 | 7.6208 | 46.8762 | 7.3 | -2.3719 | 26.71 | -82.4766 | -27.3056
161 | 0.013417 | 22.4383 | 1.5041 | 30.4507 | -0.004283 | -8.0124 | -26538.6795 | -21.1117 | 7.6007 | 46.8036 | 7.5387 | -2.7141 | 26.7662 | -82.6491 | -27.2898
162 | 0.0135 | 20.239 | 1.4998 | 28.599 | -0.0044602 | -8.3599 | -26238.8596 | -18.8178 | 7.4505 | 46.7345 | 7.7729 | -3.0775 | 26.825 | -82.8027 | -27.2773
163 | 0.013583 | 18.0658 | 1.4953 | 26.7852 | -0.0046473 | -8.7193 | -25914.5896 | -16.58 | 7.1748 | 46.6696 | 8.0022 | -3.4629 | 26.8865 | -82.9377 | -27.2684
164 | 0.013667 | 15.9206 | 1.4907 | 25.0123 | -0.004845 | -9.0917 | -25566.1857 | -14.4054 | 6.7787 | 46.6096 | 8.2264 | -3.8711 | 26.9508 | -83.0547 | -27.2634
165 | 0.01375 | 13.8054 | 1.4858 | 23.2835 | -0.005054 | -9.4781 | -25193.988 | -12.3007 | 6.2675 | 46.5552 | 8.445 | -4.303 | 27.0178 | -83.1544 | -27.2628
166 | 0.013833 | 11.7223 | 1.4808 | 21.602 | -0.005275 | -9.8797 | -24798.3601 | -10.2723 | 5.6472 | 46.5069 | 8.6577 | -4.7596 | 27.0876 | -83.2373 | -27.2668
167 | 0.013917 | 9.673 | 1.4755 | 19.9709 | -0.0055087 | -10.2978 | -24379.6886 | -8.326 | 4.924 | 46.4654 | 8.8638 | -5.242 | 27.1603 | -83.3044 | -27.2757
168 | 0.014 | 7.6596 | 1.47 | 18.3933 | -0.0057556 | -10.7337 | -23938.383 | -6.4672 | 4.1042 | 46.4313 | 9.0627 | -5.7514 | 27.2359 | -83.3562 | -27.2899
169 | 0.014083 | 5.6839 | 1.4642 | 16.8724 | -0.0060163 | -11.1885 | -23474.8751 | -4.7011 | 3.1948 | 46.405 | 9.2538 | -6.2889 | 27.3145 | -83.3938 | -27.3099
170 | 0.014167 | 3.7477 | 1.4582 | 15.4112 | -0.0062912 | -11.6635 | -22989.6186 | -3.032 | 2.2029 | 46.3871 | 9.436 | -6.8556 | 27.396 | -83.4179 | -27.336
171 | 0.01425 | 1.8529 | 1.4519 | 14.0129 | -0.0065805 | -12.16 | -22483.0886 | -1.4641 | 1.1357 | 46.3779 | 9.6083 | -7.4529 | 27.4806 | -83.4294 | -27.3685
172 | 0.014333 | 0.0011401 | 1.4453 | 12.6802 | -0.0068841 | -12.679 | -21955.7814 | -0.00087844 | 0.00072671 | 46.3779 | 9.7694 | -8.0819 | 27.5682 | -83.4295 | -27.408
173 | 0.014417 | -1.8058 | 1.4385 | 11.4159 | -0.0072014 | -13.2217 | -21408.2137 | 1.3546 | -1.1942 | 46.3874 | 9.9177 | -8.7437 | 27.6589 | -83.4189 | -27.4548
174 | 0.0145 | -3.5663 | 1.4313 | 10.2225 | -0.0075316 | -13.7888 | -20840.9221 | 2.5998 | -2.4413 | 46.4067 | 10.0516 | -9.4391 | 27.7528 | -83.3988 | -27.5095
175 | 0.014583 | -5.2788 | 1.4237 | 9.1022 | -0.0078733 | -14.381 | -20254.4628 | 3.7327 | -3.7327 | 46.4359 | 10.1689 | -10.1689 | 27.8498 | -83.3702 | -27.5723
176 | 0.014667 | -6.9416 | 1.4159 | 8.0568 | -0.0082243 | -14.9984 | -19649.411 | 4.7518 | -5.0602 | 46.4754 | 10.2671 | -10.9333 | 27.9499 | -83.3341 | -27.6439
177 | 0.01475 | -8.5532 | 1.4076 | 7.0876 | -0.0085818 | -15.6408 | -19026.3601 | 5.6563 | -6.4158 | 46.5251 | 10.3435 | -11.7324 | 28.0532 | -83.2917 | -27.7247
178 | 0.014833 | -10.1122 | 1.399 | 6.1954 | -0.0089424 | -16.3076 | -18385.9213 | 6.4457 | -7.7915 | 46.5851 | 10.3949 | -12.5652 | 28.1597 | -83.2439 | -27.8152
179 | 0.014917 | -11.617 | 1.3901 | 5.3803 | -0.0093017 | -16.9973 | -17728.7231 | 7.1202 | -9.1793 | 46.6555 | 10.4178 | -13.4305 | 28.2692 | -83.1919 | -27.9157
180 | 0.015 | -13.0665 | 1.3808 | 4.6415 | -0.0096549 | -17.708 | -17055.4104 | 7.6803 | -10.571 | 46.7362 | 10.4085 | -14.3261 | 28.3817 | -83.1367 | -28.0269
181 | 0.015083 | -14.4592 | 1.3711 | 3.9776 | -0.0099966 | -18.4367 | -16366.644 | 8.1273 | -11.9589 | 46.8271 | 10.363 | -15.2487 | 28.4971 | -83.0792 | -28.149
182 | 0.015167 | -15.7939 | 1.3612 | 3.3861 | -0.010321 | -19.18 | -15663.1001 | 8.4628 | -13.3352 | 46.9279 | 10.2771 | -16.1942 | 28.6153 | -83.0206 | -28.2825
183 | 0.01525 | -17.0693 | 1.3508 | 2.864 | -0.010623 | -19.9333 | -14945.4694 | 8.689 | -14.6923 | 47.0385 | 10.1469 | -17.1575 | 28.736 | -82.9617 | -28.4278
184 | 0.015333 | -18.2844 | 1.3402 | 2.4074 | -0.010897 | -20.6918 | -14214.4566 | 8.8086 | -16.0227 | 47.1586 | 9.9683 | -18.1323 | 28.8592 | -82.9034 | -28.585
185 | 0.015417 | -19.438 | 1.3293 | 2.0116 | -0.011138 | -21.4496 | -13470.7795 | 8.8247 | -17.3194 | 47.2879 | 9.7379 | -19.1118 | 28.9844 | -82.8467 | -28.7545
186 | 0.0155 | -20.5292 | 1.3182 | 1.6717 | -0.011343 | -22.2009 | -12715.1684 | 8.7409 | -18.5754 | 47.4259 | 9.4527 | -20.0879 | 29.1115 | -82.7924 | -28.9363
187 | 0.015583 | -21.5569 | 1.3068 | 1.3822 | -0.011508 | -22.9391 | -11948.3654 | 8.5613 | -19.784 | 47.5723 | 9.1102 | -21.0525 | 29.2401 | -82.7412 | -29.1305
188 | 0.015667 | -22.5203 | 1.2953 | 1.1378 | -0.011632 | -23.6581 | -11171.1239 | 8.2903 | -20.9388 | 47.7266 | 8.7091 | -21.9967 | 29.3698 | -82.6938 | -29.3371
189 | 0.01575 | -23.4185 | 1.2837 | 0.93299 | -0.011714 | -24.3515 | -10384.2072 | 7.9327 | -22.034 | 47.8883 | 8.2488 | -22.9119 | 29.5002 | -82.651 | -29.5559
190 | 0.015833 | -24.2508 | 1.272 | 0.76259 | -0.011754 | -25.0133 | -9588.3885 | 7.4939 | -23.0638 | 48.0568 | 7.7295 | -23.7891 | 29.631 | -82.6132 | -29.7867
191 | 0.015917 | -25.0163 | 1.2602 | 0.62171 | -0.011753 | -25.638 | -8784.4496 | 6.9793 | -24.023 | 48.2316 | 7.1528 | -24.6201 | 29.7616 | -82.581 | -30.0292
192 | 0.016 | -25.7146 | 1.2485 | 0.5059 | -0.011711 | -26.2205 | -7973.1803 | 6.395 | -24.9068 | 48.4121 | 6.5208 | -25.3968 | 29.8917 | -82.5548 | -30.283
193 | 0.016083 | -26.345 | 1.2368 | 0.41116 | -0.011631 | -26.7562 | -7155.3779 | 5.747 | -25.7105 | 48.5977 | 5.8367 | -26.1118 | 30.0208 | -82.5351 | -30.5475
194 | 0.016167 | -26.907 | 1.2251 | 0.33399 | -0.011513 | -27.241 | -6331.8459 | 5.0419 | -26.4304 | 48.7876 | 5.1045 | -26.7585 | 30.1484 | -82.5221 | -30.8224
195 | 0.01625 | -27.4002 | 1.2136 | 0.27134 | -0.01136 | -27.6715 | -5503.3935 | 4.2863 | -27.0629 | 48.9813 | 4.3288 | -27.3309 | 30.2741 | -82.5161 | -31.1068
196 | 0.016333 | -27.8241 | 1.2023 | 0.22063 | -0.011174 | -28.0448 | -4670.8348 | 3.4873 | -27.6047 | 49.178 | 3.5149 | -27.8236 | 30.3974 | -82.5172 | -31.4001
197 | 0.016417 | -28.1786 | 1.1911 | 0.17966 | -0.010955 | -28.3582 | -3834.988 | 2.6518 | -28.0535 | 49.3772 | 2.6687 | -28.2324 | 30.5179 | -82.5256 | -31.7015
198 | 0.0165 | -28.4632 | 1.1801 | 0.14661 | -0.010706 | -28.6098 | -2996.6746 | 1.7872 | -28.4071 | 49.578 | 1.7964 | -28.5534 | 30.6353 | -82.5413 | -32.0103
199 | 0.016583 | -28.678 | 1.1694 | 0.11997 | -0.010428 | -28.7979 | -2156.7184 | 0.9008 | -28.6638 | 49.7798 | 0.90457 | -28.7837 | 30.749 | -82.5644 | -32.3256
200 | 0.016667 | -28.8227 | 1.159 | 0.098515 | -0.010122 | -28.9212 | -1315.945 | 3.2659e-14 | -28.8227 | 49.9819 | 3.2771e-14 | -28.9212 | 30.8589 | -82.5946 | -32.6465
201 | 0.01675 | -28.8973 | 1.1489 | 0.081226 | -0.0097888 | -28.9785 | -475.1805 | -0.90769 | -28.883 | 50.1825 | -0.91024 | -28.9642 | 30.9639 | -82.6317 | -32.9703
202 | 0.016833 | -28.9019 | 1.1391 | 0.067288 | -0.0094301 | -28.9692 | 364.7487 | -1.8148 | -28.8449 | 50.3816 | -1.819 | -28.912 | 31.0641 | -82.6756 | -33.297
203 | 0.016917 | -28.8366 | 1.1296 | 0.056041 | -0.0090466 | -28.8926 | 1203.017 | -2.7138 | -28.7086 | 50.5789 | -2.719 | -28.7644 | 31.1594 | -82.726 | -33.6262
204 | 0.017 | -28.7015 | 1.1206 | 0.046955 | -0.0086392 | -28.7484 | 2038.8006 | -3.5972 | -28.4751 | 50.7742 | -3.6031 | -28.5217 | 31.2498 | -82.7829 | -33.9579
205 | 0.017083 | -28.4968 | 1.112 | 0.039604 | -0.0082086 | -28.5364 | 2871.2781 | -4.4579 | -28.146 | 50.9674 | -4.4641 | -28.1851 | 31.3353 | -82.8461 | -34.2918
206 | 0.017167 | -28.223 | 1.1038 | 0.033647 | -0.0077557 | -28.2567 | 3699.6313 | -5.2885 | -27.7231 | 51.1582 | -5.2948 | -27.7562 | 31.416 | -82.9153 | -34.6278
207 | 0.01725 | -27.8804 | 1.096 | 0.028812 | -0.0072811 | -27.9092 | 4523.046 | -6.0819 | -27.2089 | 51.3467 | -6.0882 | -27.237 | 31.4916 | -82.9906 | -34.9657
208 | 0.017333 | -27.4693 | 1.0887 | 0.024882 | -0.0067855 | -27.4942 | 5340.7132 | -6.8313 | -26.6063 | 51.5326 | -6.8375 | -26.6304 | 31.5624 | -83.0716 | -35.3052
209 | 0.017417 | -26.9904 | 1.0819 | 0.021685 | -0.0062697 | -27.0121 | 6151.8291 | -7.5301 | -25.9187 | 51.7157 | -7.5361 | -25.9396 | 31.6281 | -83.1582 | -35.6462
210 | 0.0175 | -26.4442 | 1.0757 | 0.019082 | -0.0057342 | -26.4633 | 6955.5966 | -8.1717 | -25.15 | 51.8959 | -8.1776 | -25.1681 | 31.6889 | -83.2503 | -35.9885
211 | 0.017583 | -25.8314 | 1.0699 | 0.016965 | -0.0051797 | -25.8484 | 7751.2259 | -8.7501 | -24.3043 | 52.0731 | -8.7558 | -24.3202 | 31.7447 | -83.3477 | -36.332
212 | 0.017667 | -25.1526 | 1.0647 | 0.015247 | -0.004607 | -25.1679 | 8537.9351 | -9.2593 | -23.3863 | 52.2472 | -9.2649 | -23.4005 | 31.7956 | -83.4502 | -36.6764
213 | 0.01775 | -24.4087 | 1.0601 | 0.01386 | -0.0040166 | -24.4225 | 9314.9511 | -9.6939 | -22.4012 | 52.418 | -9.6994 | -22.4139 | 31.8414 | -83.5577 | -37.0215
214 | 0.017833 | -23.6004 | 1.0561 | 0.012749 | -0.0034092 | -23.6132 | 10081.5105 | -10.0486 | -21.3543 | 52.5853 | -10.054 | -21.3658 | 31.8822 | -83.67 | -37.3673
215 | 0.017917 | -22.7287 | 1.0527 | 0.011874 | -0.0027856 | -22.7406 | 10836.86 | -10.3186 | -20.2515 | 52.7492 | -10.324 | -20.262 | 31.9181 | -83.7869 | -37.7134
216 | 0.018 | -21.7946 | 1.0499 | 0.011202 | -0.0021463 | -21.8058 | 11580.2574 | -10.4996 | -19.0988 | 52.9094 | -10.505 | -19.1086 | 31.949 | -83.9084 | -38.0599
217 | 0.018083 | -20.799 | 1.0478 | 0.010709 | -0.0014922 | -20.8098 | 12310.9725 | -10.5876 | -17.9026 | 53.0658 | -10.593 | -17.9118 | 31.9749 | -84.0341 | -38.4063
218 | 0.018167 | -19.7432 | 1.0463 | 0.010378 | -0.00082379 | -19.7535 | 13028.2874 | -10.5789 | -16.6697 | 53.2184 | -10.5845 | -16.6785 | 31.9958 | -84.1641 | -38.7527
219 | 0.01825 | -18.6281 | 1.0455 | 0.0102 | -0.00014194 | -18.6383 | 13731.4975 | -10.4705 | -15.4069 | 53.367 | -10.4763 | -15.4153 | 32.0118 | -84.298 | -39.0989
220 | 0.018333 | -17.455 | 1.0453 | 0.010169 | 0.00055266 | -17.4651 | 14419.9119 | -10.2598 | -14.1214 | 53.5116 | -10.2658 | -14.1296 | 32.0228 | -84.4358 | -39.4445
221 | 0.018417 | -16.2252 | 1.0459 | 0.010288 | 0.0012592 | -16.2355 | 15092.8547 | -9.9445 | -12.8204 | 53.652 | -9.9508 | -12.8285 | 32.029 | -84.5772 | -39.7896
222 | 0.0185 | -14.94 | 1.0471 | 0.010564 | 0.001977 | -14.9505 | 15749.6649 | -9.5231 | -11.5114 | 53.7881 | -9.5298 | -11.5196 | 32.0302 | -84.7222 | -40.1339
223 | 0.018583 | -13.6007 | 1.0491 | 0.011012 | 0.0027053 | -13.6117 | 16389.6975 | -8.9943 | -10.202 | 53.92 | -9.0016 | -10.2103 | 32.0265 | -84.8705 | -40.4773
224 | 0.018667 | -12.2088 | 1.0518 | 0.011654 | 0.0034432 | -12.2205 | 17012.3243 | -8.3575 | -8.8998 | 54.0474 | -8.3655 | -8.9083 | 32.018 | -85.0221 | -40.8195
225 | 0.01875 | -10.7658 | 1.0553 | 0.012522 | 0.0041898 | -10.7783 | 17616.9338 | -7.6126 | -7.6126 | 54.1704 | -7.6214 | -7.6214 | 32.0046 | -85.1767 | -41.1605
226 | 0.018833 | -9.2732 | 1.0595 | 0.013663 | 0.0049444 | -9.2868 | 18202.9328 | -6.7599 | -6.3479 | 54.2888 | -6.7698 | -6.3573 | 31.9865 | -85.3342 | -41.5001
227 | 0.018917 | -7.7325 | 1.0644 | 0.015137 | 0.005706 | -7.7477 | 18769.7459 | -5.8002 | -5.1136 | 54.4026 | -5.8116 | -5.1236 | 31.9635 | -85.4945 | -41.8381
228 | 0.019 | -6.1454 | 1.0701 | 0.017026 | 0.0064737 | -6.1625 | 19316.8172 | -4.7351 | -3.9172 | 54.5117 | -4.7483 | -3.9281 | 31.9359 | -85.6574 | -42.1743
229 | 0.019083 | -4.5136 | 1.0766 | 0.019442 | 0.0072465 | -4.5331 | 19843.6098 | -3.5665 | -2.7664 | 54.6161 | -3.5818 | -2.7783 | 31.9035 | -85.8227 | -42.5086
230 | 0.019167 | -2.8387 | 1.0838 | 0.022534 | 0.0080233 | -2.8613 | 20349.6071 | -2.2966 | -1.6686 | 54.7157 | -2.3148 | -1.6818 | 31.8665 | -85.9904 | -42.8409
231 | 0.01925 | -1.1226 | 1.0918 | 0.026504 | 0.0088028 | -1.1491 | 20834.3129 | -0.92848 | -0.631 | 54.8104 | -0.9504 | -0.64589 | 31.8248 | -86.1602 | -43.1709
232 | 0.019333 | 0.63303 | 1.1006 | 0.031625 | 0.0095838 | 0.60141 | 21297.2519 | 0.53449 | 0.3392 | 54.9002 | 0.50779 | 0.32225 | 31.7786 | -86.332 | -43.4986
233 | 0.019417 | 2.4263 | 1.1102 | 0.038271 | 0.010365 | 2.3881 | 21737.9705 | 2.0884 | 1.2351 | 54.9852 | 2.0555 | 1.2156 | 31.7278 | -86.5057 | -43.8237
234 | 0.0195 | 4.2554 | 1.1206 | 0.046952 | 0.011143 | 4.2084 | 22156.0369 | 3.729 | 2.0501 | 55.0651 | 3.6879 | 2.0274 | 31.6725 | -86.681 | -44.1462
235 | 0.019583 | 6.1184 | 1.1317 | 0.058371 | 0.011918 | 6.06 | 22551.0417 | 5.4515 | 2.7777 | 55.1401 | 5.3995 | 2.7512 | 31.6128 | -86.858 | -44.4659
236 | 0.019667 | 8.0133 | 1.1437 | 0.073499 | 0.012685 | 7.9398 | 22922.5981 | 7.2506 | 3.4119 | 55.21 | 7.1841 | 3.3806 | 31.5486 | -87.0364 | -44.7826
237 | 0.01975 | 9.9381 | 1.1563 | 0.093687 | 0.013442 | 9.8444 | 23270.3425 | 9.1208 | 3.9469 | 55.2749 | 9.0348 | 3.9097 | 31.4801 | -87.2161 | -45.0963
238 | 0.019833 | 11.891 | 1.1698 | 0.12081 | 0.014183 | 11.7702 | 23593.935 | 11.0559 | 4.3774 | 55.3347 | 10.9436 | 4.3329 | 31.4072 | -87.3969 | -45.4069
239 | 0.019917 | 13.8698 | 1.184 | 0.15749 | 0.014902 | 13.7123 | 23893.0593 | 13.0498 | 4.6982 | 55.3893 | 12.9016 | 4.6449 | 31.3301 | -87.5788 | -45.7143
240 | 0.02 | 15.8725 | 1.1989 | 0.20738 | 0.015591 | 15.6651 | 24167.4232 | 15.0956 | 4.9049 | 55.4389 | 14.8984 | 4.8408 | 31.2486 | -87.7615 | -46.0184
241 | 0.020083 | 17.897 | 1.2145 | 0.27556 | 0.016238 | 17.6214 | 24416.7591 | 17.1864 | 4.9931 | 55.4834 | 16.9217 | 4.9162 | 31.1628 | -87.945 | -46.3194
242 | 0.020167 | 19.9412 | 1.2307 | 0.36908 | 0.016829 | 19.5721 | 24640.824 | 19.3147 | 4.9592 | 55.5227 | 18.9572 | 4.8674 | 31.0726 | -88.129 | -46.6172
243 | 0.02025 | 22.0031 | 1.2475 | 0.49761 | 0.017343 | 21.5055 | 24839.3998 | 21.4732 | 4.7998 | 55.5569 | 20.9875 | 4.6913 | 30.978 | -88.3135 | -46.9122
244 | 0.020333 | 24.0804 | 1.2649 | 0.6742 | 0.017755 | 23.4062 | 25012.2937 | 23.6539 | 4.5122 | 55.5859 | 22.9916 | 4.3859 | 30.8788 | -88.4984 | -47.2046
245 | 0.020417 | 26.1711 | 1.2826 | 0.91617 | 0.018037 | 25.2549 | 25159.3381 | 25.8489 | 4.0941 | 55.6099 | 24.944 | 3.9507 | 30.7749 | -88.6835 | -47.4949
246 | 0.0205 | 28.2729 | 1.3007 | 1.2457 | 0.018156 | 27.0272 | 25280.3909 | 28.05 | 3.5435 | 55.6287 | 26.8141 | 3.3874 | 30.6657 | -88.8686 | -47.7838
247 | 0.020583 | 30.3837 | 1.3188 | 1.6899 | 0.018079 | 28.6939 | 25375.3356 | 30.2489 | 2.8594 | 55.6424 | 28.5665 | 2.7003 | 30.551 | -89.0536 | -48.0723
248 | 0.020667 | 32.5014 | 1.3369 | 2.28 | 0.017783 | 30.2214 | 25444.0817 | 32.4373 | 2.0408 | 55.651 | 30.1617 | 1.8976 | 30.4299 | -89.2385 | -48.3616
249 | 0.02075 | 34.6237 | 1.3547 | 3.0493 | 0.017258 | 31.5744 | 25486.5643 | 34.6066 | 1.0876 | 55.6545 | 31.5589 | 0.99178 | 30.3016 | -89.423 | -48.6532
250 | 0.020833 | 36.7484 | 1.3719 | 4.0285 | 0.01652 | 32.7199 | 25502.7444 | 36.7484 | 4.389e-14 | 55.653 | 32.7199 | 3.9079e-14 | 30.1651 | -89.6071 | -48.9488
251 | 0.020917 | 38.8734 | 1.3885 | 5.2421 | 0.015604 | 33.6313 | 25492.6091 | 38.8542 | -1.221 | 55.6465 | 33.6147 | -1.0564 | 30.019 | -89.7906 | -49.2502
252 | 0.021 | 40.9965 | 1.4041 | 6.7033 | 0.014568 | 34.2932 | 25456.1715 | 40.9156 | -2.5742 | 55.6349 | 34.2255 | -2.1533 | 29.862 | -89.9733 | -49.5593
253 | 0.021083 | 43.1154 | 1.4186 | 8.4122 | 0.013471 | 34.7032 | 25393.4704 | 42.924 | -4.0575 | 55.6185 | 34.5492 | -3.2659 | 29.6925 | -90.1553 | -49.8777
254 | 0.021167 | 45.228 | 1.4321 | 10.3564 | 0.01237 | 34.8716 | 25304.5708 | 44.8714 | -5.6686 | 55.597 | 34.5966 | -4.3706 | 29.5091 | -90.3362 | -50.207
255 | 0.02125 | 47.3321 | 1.4445 | 12.5136 | 0.011308 | 34.8185 | 25189.5633 | 46.7494 | -7.4044 | 55.5707 | 34.3898 | -5.4468 | 29.3103 | -90.5161 | -50.5482
256 | 0.021333 | 49.4255 | 1.4558 | 14.8556 | 0.010314 | 34.5699 | 25048.5645 | 48.5501 | -9.2614 | 55.5396 | 33.9576 | -6.4777 | 29.0947 | -90.6948 | -50.9021
257 | 0.021417 | 51.5061 | 1.4661 | 17.3517 | 0.0094001 | 34.1544 | 24881.7163 | 50.2657 | -11.2357 | 55.5036 | 33.3319 | -7.4506 | 28.8613 | -90.8721 | -51.2691
258 | 0.0215 | 53.5718 | 1.4755 | 19.9713 | 0.0085726 | 33.6004 | 24689.1865 | 51.8887 | -13.3228 | 55.4629 | 32.5448 | -8.3561 | 28.6088 | -91.048 | -51.6492
259 | 0.021583 | 55.6203 | 1.4841 | 22.686 | 0.0078289 | 32.9343 | 24471.168 | 53.4118 | -15.5176 | 55.4175 | 31.6266 | -9.1884 | 28.3366 | -91.2223 | -52.0421
260 | 0.021667 | 57.6496 | 1.4919 | 25.4699 | 0.0071637 | 32.1797 | 24227.8788 | 54.828 | -17.8147 | 55.3675 | 30.6047 | -9.9441 | 28.0437 | -91.3948 | -52.4472
261 | 0.02175 | 59.6576 | 1.4991 | 28.3006 | 0.0065695 | 31.357 | 23959.5621 | 56.1307 | -20.2083 | 55.3129 | 29.5032 | -10.6218 | 27.7298 | -91.5656 | -52.8639
262 | 0.021833 | 61.6422 | 1.5056 | 31.1584 | 0.0060387 | 30.4837 | 23666.4854 | 57.3134 | -22.692 | 55.2538 | 28.343 | -11.2218 | 27.3942 | -91.7344 | -53.2909
263 | 0.021917 | 63.6013 | 1.5117 | 34.0267 | 0.0055638 | 29.5746 | 23348.9411 | 58.3704 | -25.2591 | 55.1902 | 27.1423 | -11.7455 | 27.0369 | -91.9011 | -53.7271
264 | 0.022 | 65.533 | 1.5172 | 36.891 | 0.005138 | 28.642 | 23007.2453 | 59.296 | -27.9026 | 55.1223 | 25.916 | -12.1952 | 26.6578 | -92.0657 | -54.171
265 | 0.022083 | 67.4352 | 1.5224 | 39.7394 | 0.004755 | 27.6958 | 22641.7381 | 60.0852 | -30.6149 | 55.05 | 24.6771 | -12.5736 | 26.2571 | -92.2279 | -54.6207
266 | 0.022167 | 69.306 | 1.5271 | 42.5616 | 0.0044094 | 26.7444 | 22252.7832 | 60.7333 | -33.3884 | 54.9735 | 23.4363 | -12.8842 | 25.8357 | -92.3878 | -55.0737
267 | 0.02225 | 71.1433 | 1.5315 | 45.3488 | 0.0040966 | 25.7946 | 21840.7673 | 61.2361 | -36.2149 | 54.8929 | 22.2025 | -13.1305 | 25.395 | -92.5451 | -55.5272
268 | 0.022333 | 72.9455 | 1.5356 | 48.0937 | 0.0038123 | 24.8518 | 21406.0999 | 61.5899 | -39.0861 | 54.8082 | 20.9831 | -13.3163 | 24.9376 | -92.6997 | -55.9767
269 | 0.022417 | 74.7104 | 1.5394 | 50.79 | 0.0035531 | 23.9204 | 20949.2129 | 61.7915 | -41.9935 | 54.7195 | 19.7841 | -13.4453 | 24.4675 | -92.8516 | -56.4172
270 | 0.0225 | 76.4364 | 1.543 | 53.4325 | 0.003316 | 23.0039 | 20470.5599 | 61.8383 | -44.9282 | 54.6269 | 18.6106 | -13.5214 | 23.99 | -93.0006 | -56.8423
271 | 0.022583 | 78.1216 | 1.5463 | 56.0165 | 0.0030982 | 22.1051 | 19970.6162 | 61.7282 | -47.8813 | 54.5305 | 17.4664 | -13.5484 | 23.5108 | -93.1466 | -57.2458
272 | 0.022667 | 79.7642 | 1.5494 | 58.5383 | 0.0028975 | 21.226 | 19449.878 | 61.4594 | -50.8436 | 54.4303 | 16.3549 | -13.5299 | 23.0355 | -93.2895 | -57.6223
273 | 0.02275 | 81.3627 | 1.5523 | 60.9945 | 0.002712 | 20.3682 | 18908.8621 | 61.031 | -53.8061 | 54.3266 | 15.2784 | -13.4697 | 22.5684 | -93.4292 | -57.9677
274 | 0.022833 | 82.9152 | 1.555 | 63.3823 | 0.0025399 | 19.5329 | 18348.1052 | 60.4426 | -56.7593 | 54.2193 | 14.2388 | -13.3712 | 22.1128 | -93.5656 | -58.2791
275 | 0.022917 | 84.4201 | 1.5576 | 65.6993 | 0.0023798 | 18.7208 | 17768.1636 | 59.6941 | -59.6941 | 54.1086 | 13.2376 | -13.2376 | 21.671 | -93.6986 | -58.5549
276 | 0.023 | 85.876 | 1.5599 | 67.9435 | 0.0022303 | 17.9325 | 17169.6124 | 58.7862 | -62.6009 | 53.9946 | 12.2757 | -13.0722 | 21.2445 | -93.828 | -58.7944
277 | 0.023083 | 87.2812 | 1.5622 | 70.113 | 0.0020904 | 17.1682 | 16553.0451 | 57.7201 | -65.4706 | 53.8774 | 11.3536 | -12.8781 | 20.8343 | -93.9538 | -58.9973
278 | 0.023167 | 88.6344 | 1.5643 | 72.2064 | 0.0019591 | 16.428 | 15919.073 | 56.4977 | -68.294 | 53.7571 | 10.4716 | -12.658 | 20.441 | -94.0758 | -59.164
279 | 0.02325 | 89.934 | 1.5662 | 74.2223 | 0.0018355 | 15.7117 | 15268.3245 | 55.1212 | -71.0618 | 53.6339 | 9.6298 | -12.4147 | 20.0649 | -94.194 | -59.2952
280 | 0.023333 | 91.1786 | 1.5681 | 76.1596 | 0.0017187 | 15.0191 | 14601.4447 | 53.5935 | -73.7651 | 53.5077 | 8.828 | -12.1507 | 19.706 | -94.3082 | -59.3919
281 | 0.023417 | 92.3671 | 1.5698 | 78.0174 | 0.0016082 | 14.3497 | 13919.0944 | 51.918 | -76.395 | 53.3788 | 8.0658 | -11.8684 | 19.3643 | -94.4184 | -59.4554
282 | 0.0235 | 93.4981 | 1.5714 | 79.7948 | 0.0015033 | 13.7033 | 13221.9498 | 50.0988 | -78.943 | 53.2472 | 7.3426 | -11.5701 | 19.0395 | -94.5244 | -59.487
283 | 0.023583 | 94.5704 | 1.5729 | 81.4913 | 0.0014035 | 13.0791 | 12510.7016 | 48.1402 | -81.4007 | 53.1132 | 6.6578 | -11.2577 | 18.7314 | -94.6262 | -59.4885
284 | 0.023667 | 95.5828 | 1.5743 | 83.1061 | 0.0013084 | 12.4767 | 11786.0547 | 46.0474 | -83.7599 | 52.9767 | 6.0107 | -10.9334 | 18.4396 | -94.7237 | -59.4614
285 | 0.02375 | 96.5344 | 1.5756 | 84.6389 | 0.0012173 | 11.8954 | 11048.7268 | 43.8257 | -86.0127 | 52.838 | 5.4004 | -10.5989 | 18.1636 | -94.8167 | -59.4075
286 | 0.023833 | 97.424 | 1.5768 | 86.0893 | 0.0011301 | 11.3346 | 10299.4483 | 41.4811 | -88.1518 | 52.6972 | 4.826 | -10.2559 | 17.9031 | -94.9052 | -59.3288
287 | 0.023917 | 98.2506 | 1.5779 | 87.457 | 0.0010464 | 10.7936 | 9538.9614 | 39.02 | -90.17 | 52.5544 | 4.2866 | -9.9059 | 17.6576 | -94.9891 | -59.2272
288 | 0.024 | 99.0135 | 1.579 | 88.7418 | 0.0009657 | 10.2717 | 8768.0194 | 36.4493 | -92.0604 | 52.4097 | 3.7813 | -9.5503 | 17.4265 | -95.0683 | -59.1045
289 | 0.024083 | 99.7117 | 1.58 | 89.9436 | 0.00088789 | 9.7681 | 7987.3858 | 33.7761 | -93.8168 | 52.2632 | 3.3088 | -9.1907 | 17.2094 | -95.1427 | -58.9627
290 | 0.024167 | 100.3445 | 1.5808 | 91.0621 | 0.00081266 | 9.2823 | 7197.8338 | 31.0081 | -95.4333 | 52.1152 | 2.8684 | -8.828 | 17.0057 | -95.2123 | -58.8037
291 | 0.02425 | 100.9111 | 1.5817 | 92.0976 | 0.00073978 | 8.8135 | 6400.1451 | 28.1533 | -96.9043 | 51.9657 | 2.4589 | -8.4636 | 16.8149 | -95.2769 | -58.6295
292 | 0.024333 | 101.411 | 1.5824 | 93.0499 | 0.00066902 | 8.361 | 5595.1098 | 25.2199 | -98.2249 | 51.8149 | 2.0793 | -8.0984 | 16.6365 | -95.3366 | -58.4418
293 | 0.024417 | 101.8434 | 1.5831 | 93.9193 | 0.0006002 | 7.9242 | 4783.525 | 22.2165 | -99.3907 | 51.663 | 1.7286 | -7.7333 | 16.4698 | -95.3912 | -58.2426
294 | 0.0245 | 102.2081 | 1.5837 | 94.7058 | 0.00053313 | 7.5023 | 3966.1944 | 19.1519 | -100.3977 | 51.5099 | 1.4058 | -7.3694 | 16.3145 | -95.4406 | -58.0335
295 | 0.024583 | 102.5043 | 1.5842 | 95.4097 | 0.00046765 | 7.0947 | 3143.9271 | 16.0352 | -101.2423 | 51.3561 | 1.1099 | -7.0073 | 16.1699 | -95.4848 | -57.8162
296 | 0.024667 | 102.7319 | 1.5847 | 96.0312 | 0.00040359 | 6.7007 | 2317.5374 | 12.8757 | -101.9219 | 51.2014 | 0.83982 | -6.6479 | 16.0355 | -95.5237 | -57.5923
297 | 0.02475 | 102.8905 | 1.5851 | 96.5707 | 0.00034083 | 6.3198 | 1487.8436 | 9.6829 | -102.4339 | 51.0462 | 0.59474 | -6.2917 | 15.9109 | -95.5574 | -57.3633
298 | 0.024833 | 102.9798 | 1.5854 | 97.0286 | 0.00027921 | 5.9513 | 655.6669 | 6.4662 | -102.7766 | 50.8905 | 0.37368 | -5.9395 | 15.7955 | -95.5856 | -57.1306
299 | 0.024917 | 102.9997 | 1.5857 | 97.4052 | 0.00021863 | 5.5945 | -178.1685 | 3.2353 | -102.9489 | 50.7346 | 0.17573 | -5.5918 | 15.6887 | -95.6085 | -56.8955
300 | 0.025 | 102.9501 | 1.5859 | 97.7011 | 0.00015896 | 5.249 | -1012.8373 | 2.207e-13 | -102.9501 | 50.5784 | 1.1253e-14 | -5.249 | 15.5903 | -95.6258 | -56.6592
301 | 0.025083 | 102.8309 | 1.5861 | 97.9168 | 0.00010009 | 4.9142 | -1847.513 | -3.23 | -102.7802 | 50.4223 | -0.15436 | -4.9117 | 15.4995 | -95.6377 | -56.4228
302 | 0.025167 | 102.6422 | 1.5862 | 98.0528 | 4.1922e-05 | 4.5894 | -2681.3693 | -6.445 | -102.4397 | 50.2664 | -0.28817 | -4.5804 | 15.4161 | -95.644 | -56.1873
303 | 0.02525 | 102.3841 | 1.5862 | 98.1098 | -1.5646e-05 | 4.2743 | -3513.5807 | -9.6352 | -101.9297 | 50.1108 | -0.40224 | -4.2553 | 15.3396 | -95.6448 | -55.9537
304 | 0.025333 | 102.0567 | 1.5862 | 98.0885 | -7.2705e-05 | 3.9682 | -4343.3231 | -12.7911 | -101.2519 | 49.9556 | -0.49734 | -3.9369 | 15.2695 | -95.6399 | -55.7228
305 | 0.025417 | 101.6603 | 1.5861 | 97.9897 | -0.00012935 | 3.6706 | -5169.7753 | -15.9032 | -100.4087 | 49.801 | -0.57421 | -3.6254 | 15.2055 | -95.6295 | -55.4951
306 | 0.0255 | 101.1952 | 1.586 | 97.814 | -0.00018566 | 3.3812 | -5992.1189 | -18.9621 | -99.4027 | 49.6472 | -0.63357 | -3.3213 | 15.1471 | -95.6134 | -55.2715
307 | 0.025583 | 100.6617 | 1.5858 | 97.5624 | -0.00024172 | 3.0993 | -6809.5398 | -21.9587 | -98.2375 | 49.4944 | -0.67609 | -3.0247 | 15.094 | -95.5917 | -55.0524
308 | 0.025667 | 100.0604 | 1.5856 | 97.2358 | -0.00029761 | 2.8246 | -7621.2287 | -24.884 | -96.9168 | 49.3426 | -0.70246 | -2.7359 | 15.0459 | -95.5644 | -54.8384
309 | 0.02575 | 99.3917 | 1.5853 | 96.835 | -0.00035342 | 2.5567 | -8426.3821 | -27.7294 | -95.4452 | 49.192 | -0.71329 | -2.4551 | 15.0023 | -95.5315 | -54.6296
310 | 0.025833 | 98.6562 | 1.5849 | 96.3612 | -0.00040921 | 2.295 | -9224.2026 | -30.4864 | -93.8276 | 49.0428 | -0.70919 | -2.1827 | 14.963 | -95.493 | -54.4266
311 | 0.025917 | 97.8546 | 1.5845 | 95.8153 | -0.00046507 | 2.0392 | -10013.9005 | -33.1471 | -92.0695 | 48.8951 | -0.69076 | -1.9187 | 14.9276 | -95.4488 | -54.2296
312 | 0.026 | 96.9875 | 1.584 | 95.1985 | -0.00052107 | 1.7889 | -10794.6938 | -35.7035 | -90.1767 | 48.7492 | -0.65855 | -1.6633 | 14.8959 | -95.3991 | -54.0386
313 | 0.026083 | 96.0557 | 1.5835 | 94.512 | -0.00057728 | 1.5437 | -11565.8093 | -38.1483 | -88.1556 | 48.605 | -0.61309 | -1.4168 | 14.8676 | -95.3439 | -53.854
314 | 0.026167 | 95.0601 | 1.5829 | 93.7569 | -0.00063379 | 1.3033 | -12326.4837 | -40.4746 | -86.013 | 48.4628 | -0.5549 | -1.1792 | 14.8424 | -95.2832 | -53.6756
315 | 0.02625 | 94.0016 | 1.5823 | 92.9345 | -0.00069066 | 1.0671 | -13075.9635 | -42.6758 | -83.7561 | 48.3227 | -0.48447 | -0.95083 | 14.8201 | -95.217 | -53.5037
316 | 0.026333 | 92.8811 | 1.5816 | 92.0461 | -0.00074798 | 0.83501 | -13813.5067 | -44.7458 | -81.3924 | 48.1849 | -0.40227 | -0.73172 | 14.8005 | -95.1454 | -53.3381
317 | 0.026417 | 91.6997 | 1.5809 | 91.0932 | -0.00080582 | 0.60652 | -14538.3828 | -46.679 | -78.9298 | 48.0494 | -0.30874 | -0.52205 | 14.7834 | -95.0685 | -53.1789
318 | 0.0265 | 90.4584 | 1.5801 | 90.0771 | -0.00086427 | 0.38132 | -15249.874 | -48.4701 | -76.3766 | 47.9166 | -0.20432 | -0.32196 | 14.7685 | -94.9864 | -53.0259
319 | 0.026583 | 89.1585 | 1.5792 | 88.9994 | -0.0009234 | 0.15909 | -15947.2755 | -50.1145 | -73.7412 | 47.7863 | -0.089424 | -0.13158 | 14.7556 | -94.899 | -52.8791
320 | 0.026667 | 87.801 | 1.5783 | 87.8615 | -0.00098331 | -0.060509 | -16629.8967 | -51.6081 | -71.0325 | 47.6589 | 0.035567 | 0.048953 | 14.7447 | -94.8066 | -52.7383
321 | 0.02675 | 86.3872 | 1.5773 | 86.6651 | -0.0010441 | -0.27781 | -17297.0613 | -52.9474 | -68.2593 | 47.5345 | 0.17027 | 0.21951 | 14.7355 | -94.7091 | -52.6034
322 | 0.026833 | 84.9186 | 1.5763 | 85.4117 | -0.0011058 | -0.49313 | -17948.1084 | -54.1291 | -65.4309 | 47.4131 | 0.31433 | 0.37996 | 14.7278 | -94.6068 | -52.4743
323 | 0.026917 | 83.3964 | 1.5751 | 84.1032 | -0.0011686 | -0.7068 | -18582.3931 | -55.151 | -62.5565 | 47.2949 | 0.46741 | 0.53018 | 14.7216 | -94.4996 | -52.3506
324 | 0.027 | 81.822 | 1.574 | 82.7411 | -0.0012325 | -0.91912 | -19199.2869 | -56.011 | -59.6457 | 47.18 | 0.62918 | 0.67001 | 14.7168 | -94.3878 | -52.2324
325 | 0.027083 | 80.197 | 1.5727 | 81.3274 | -0.0012977 | -1.1304 | -19798.1785 | -56.7078 | -56.7078 | 47.0686 | 0.79934 | 0.79934 | 14.7131 | -94.2713 | -52.1192
326 | 0.027167 | 78.5228 | 1.5714 | 79.8639 | -0.0013642 | -1.341 | -20378.4744 | -57.2407 | -53.7526 | 46.9607 | 0.97758 | 0.918 | 14.7106 | -94.1505 | -52.0111
327 | 0.02725 | 76.8011 | 1.5701 | 78.3524 | -0.0014323 | -1.5513 | -20939.5995 | -57.6094 | -50.7895 | 46.8565 | 1.1636 | 1.0259 | 14.709 | -94.0253 | -51.9076
328 | 0.027333 | 75.0334 | 1.5686 | 76.7949 | -0.0015019 | -1.7614 | -21480.9975 | -57.8143 | -47.8281 | 46.756 | 1.3572 | 1.1228 | 14.7084 | -93.896 | -51.8086
329 | 0.027417 | 73.2215 | 1.5671 | 75.1934 | -0.0015734 | -1.9719 | -22002.1317 | -57.8563 | -44.878 | 46.6594 | 1.5581 | 1.2086 | 14.7085 | -93.7627 | -51.7139
330 | 0.0275 | 71.367 | 1.5656 | 73.55 | -0.0016467 | -2.183 | -22502.4854 | -57.7371 | -41.9485 | 46.5668 | 1.7661 | 1.2831 | 14.7095 | -93.6256 | -51.6233
331 | 0.027583 | 69.4717 | 1.5639 | 71.8666 | -0.0017221 | -2.395 | -22981.5623 | -57.4587 | -39.0489 | 46.4782 | 1.9808 | 1.3462 | 14.7111 | -93.4847 | -51.5365
332 | 0.027667 | 67.5373 | 1.5622 | 70.1456 | -0.0017998 | -2.6083 | -23438.8872 | -57.0237 | -36.1883 | 46.3938 | 2.2023 | 1.3976 | 14.7134 | -93.3404 | -51.4533
333 | 0.02775 | 65.5658 | 1.5604 | 68.3891 | -0.0018798 | -2.8233 | -23874.0064 | -56.4352 | -33.3757 | 46.3137 | 2.4301 | 1.4372 | 14.7163 | -93.1927 | -51.3735
334 | 0.027833 | 63.559 | 1.5585 | 66.5993 | -0.0019625 | -3.0403 | -24286.4879 | -55.6971 | -30.6198 | 46.2378 | 2.6643 | 1.4647 | 14.7197 | -93.0419 | -51.2968
335 | 0.027917 | 61.5187 | 1.5566 | 64.7785 | -0.002048 | -3.2598 | -24675.9225 | -54.8136 | -27.9289 | 46.1663 | 2.9045 | 1.4799 | 14.7237 | -92.8881 | -51.2231
336 | 0.028 | 59.447 | 1.5545 | 62.9291 | -0.0021366 | -3.4821 | -25041.9232 | -53.7892 | -25.3113 | 46.0993 | 3.1507 | 1.4826 | 14.7281 | -92.7316 | -51.1521
337 | 0.028083 | 57.3457 | 1.5524 | 61.0534 | -0.0022286 | -3.7077 | -25384.1266 | -52.6293 | -22.7747 | 46.0367 | 3.4028 | 1.4725 | 14.733 | -92.5725 | -51.0837
338 | 0.028167 | 55.2169 | 1.5502 | 59.154 | -0.0023241 | -3.937 | -25702.1924 | -51.3394 | -20.3267 | 45.9788 | 3.6606 | 1.4493 | 14.7383 | -92.4111 | -51.0175
339 | 0.02825 | 53.0627 | 1.5478 | 57.2333 | -0.0024236 | -4.1706 | -25995.8045 | -49.9257 | -17.9743 | 45.9254 | 3.924 | 1.4127 | 14.744 | -92.2475 | -50.9535
340 | 0.028333 | 50.885 | 1.5454 | 55.2938 | -0.0025273 | -4.4088 | -26264.6706 | -48.3945 | -15.7243 | 45.8767 | 4.193 | 1.3624 | 14.7502 | -92.0819 | -50.8914
341 | 0.028417 | 48.6859 | 1.5429 | 53.3382 | -0.0026356 | -4.6523 | -26508.5231 | -46.7528 | -13.5829 | 45.8327 | 4.4676 | 1.2979 | 14.7567 | -91.9147 | -50.8311
342 | 0.0285 | 46.4676 | 1.5402 | 51.3692 | -0.002749 | -4.9016 | -26727.119 | -45.0077 | -11.556 | 45.7934 | 4.7476 | 1.219 | 14.7637 | -91.7459 | -50.7723
343 | 0.028583 | 44.2321 | 1.5375 | 49.3895 | -0.0028679 | -5.1574 | -26920.2401 | -43.1669 | -9.6489 | 45.7589 | 5.0332 | 1.1251 | 14.7712 | -91.5759 | -50.7148
344 | 0.028667 | 41.9816 | 1.5346 | 47.4019 | -0.0029928 | -5.4203 | -27087.6935 | -41.238 | -7.8666 | 45.7291 | 5.3243 | 1.0157 | 14.779 | -91.4048 | -50.6586
345 | 0.02875 | 39.7182 | 1.5316 | 45.4093 | -0.0031242 | -5.6911 | -27229.3115 | -39.2292 | -6.2133 | 45.7042 | 5.621 | 0.89028 | 14.7874 | -91.2329 | -50.6035
346 | 0.028833 | 37.4441 | 1.5285 | 43.4146 | -0.0032628 | -5.9704 | -27344.9522 | -37.1489 | -4.693 | 45.684 | 5.9234 | 0.7483 | 14.7962 | -91.0604 | -50.5492
347 | 0.028917 | 35.1615 | 1.5252 | 41.4208 | -0.0034093 | -6.2593 | -27434.499 | -35.0054 | -3.309 | 45.6686 | 6.2315 | 0.58905 | 14.8056 | -90.8875 | -50.4956
348 | 0.029 | 32.8724 | 1.5218 | 39.431 | -0.0035643 | -6.5586 | -27497.8613 | -32.8076 | -2.0641 | 45.658 | 6.5456 | 0.41182 | 14.8155 | -90.7144 | -50.4426
349 | 0.029083 | 30.5792 | 1.5183 | 37.4485 | -0.0037287 | -6.8693 | -27534.9741 | -30.5641 | -0.96052 | 45.6521 | 6.8659 | 0.21577 | 14.826 | -90.5414 | -50.3901
350 | 0.029167 | 28.284 | 1.5145 | 35.4765 | -0.0039035 | -7.1925 | -27545.7985 | -28.284 | -1.2123e-14 | 45.651 | 7.1925 | 3.0829e-15 | 14.8372 | -90.3687 | -50.3379
351 | 0.02925 | 25.989 | 1.5106 | 33.5184 | -0.0040898 | -7.5294 | -27530.3215 | -25.9762 | 0.81633 | 45.6547 | 7.5257 | -0.2365 | 14.8491 | -90.1965 | -50.2859
352 | 0.029333 | 23.6963 | 1.5065 | 31.5777 | -0.0042885 | -7.8814 | -27488.5562 | -23.6496 | 1.4879 | 45.663 | 7.8658 | -0.49488 | 14.8618 | -90.025 | -50.234
353 | 0.029417 | 21.4083 | 1.5023 | 29.6582 | -0.0045011 | -8.2499 | -27420.5413 | -21.3133 | 2.0147 | 45.676 | 8.2133 | -0.77639 | 14.8754 | -89.8545 | -50.1821
354 | 0.0295 | 19.127 | 1.4978 | 27.7635 | -0.0047289 | -8.6365 | -27326.3418 | -18.9762 | 2.3972 | 45.6936 | 8.5684 | -1.0824 | 14.8899 | -89.6851 | -50.1301
355 | 0.029583 | 16.8546 | 1.493 | 25.8977 | -0.0049734 | -9.043 | -27206.0482 | -16.6471 | 2.6366 | 45.7158 | 8.9317 | -1.4146 | 14.9055 | -89.5171 | -50.0778
356 | 0.029667 | 14.5934 | 1.4881 | 24.0647 | -0.0052365 | -9.4713 | -27059.7771 | -14.3349 | 2.7345 | 45.7425 | 9.3036 | -1.7748 | 14.9222 | -89.3507 | -50.0254
357 | 0.02975 | 12.3454 | 1.4828 | 22.2689 | -0.0055198 | -9.9235 | -26887.6705 | -12.0481 | 2.6931 | 45.7736 | 9.6845 | -2.1648 | 14.9402 | -89.1861 | -49.9726
358 | 0.029833 | 10.1128 | 1.4773 | 20.5147 | -0.0058253 | -10.402 | -26689.896 | -9.7951 | 2.5149 | 45.8092 | 10.0752 | -2.5869 | 14.9596 | -89.0234 | -49.9195
359 | 0.029917 | 7.8978 | 1.4715 | 18.8069 | -0.0061553 | -10.9091 | -26466.6465 | -7.5842 | 2.2034 | 45.849 | 10.4759 | -3.0435 | 14.9805 | -88.863 | -49.866
360 | 0.03 | 5.7024 | 1.4653 | 17.15 | -0.0065117 | -11.4477 | -26218.14 | -5.4233 | 1.7621 | 45.8932 | 10.8874 | -3.5375 | 15.0032 | -88.7048 | -49.8122
361 | 0.030083 | 3.5288 | 1.4588 | 15.5493 | -0.0068969 | -12.0206 | -25944.6196 | -3.3201 | 1.1953 | 45.9415 | 11.3099 | -4.0718 | 15.0277 | -88.5493 | -49.7582
362 | 0.030167 | 1.379 | 1.4519 | 14.0098 | -0.0073128 | -12.6309 | -25646.3528 | -1.2821 | 0.50763 | 45.9938 | 11.7439 | -4.6497 | 15.0544 | -88.3964 | -49.704
363 | 0.03025 | -0.74495 | 1.4446 | 12.5369 | -0.0077614 | -13.2818 | -25323.632 | 0.68368 | -0.29585 | 46.0502 | 12.1894 | -5.2748 | 15.0833 | -88.2464 | -49.6496
364 | 0.030333 | -2.841 | 1.4368 | 11.1357 | -0.008244 | -13.9767 | -24976.7732 | 2.5706 | -1.2096 | 46.1105 | 12.6465 | -5.951 | 15.1148 | -88.0995 | -49.5955
365 | 0.030417 | -4.9071 | 1.4286 | 9.8116 | -0.0087614 | -14.7187 | -24606.1166 | 4.3722 | -2.2278 | 46.1746 | 13.1144 | -6.6821 | 15.149 | -87.9557 | -49.5416
366 | 0.0305 | -6.9413 | 1.4198 | 8.5696 | -0.0093135 | -15.511 | -24212.0257 | 6.0827 | -3.344 | 46.2424 | 13.5924 | -7.4725 | 15.1862 | -87.8153 | -49.4884
367 | 0.030583 | -8.9418 | 1.4105 | 7.4145 | -0.0098987 | -16.3563 | -23794.8872 | 7.6966 | -4.5517 | 46.3138 | 14.0785 | -8.326 | 15.2268 | -87.6784 | -49.4362
368 | 0.030667 | -10.9065 | 1.4006 | 6.3503 | -0.010514 | -17.2568 | -23355.1106 | 9.2087 | -5.844 | 46.3887 | 14.5704 | -9.2467 | 15.2709 | -87.5452 | -49.3855
369 | 0.03075 | -12.8337 | 1.3901 | 5.3802 | -0.011154 | -18.2139 | -22893.1277 | 10.6145 | -7.2136 | 46.467 | 15.0644 | -10.2377 | 15.3188 | -87.4156 | -49.3368
370 | 0.030833 | -14.7214 | 1.379 | 4.5064 | -0.011811 | -19.2278 | -22409.3922 | 11.9099 | -8.653 | 46.5486 | 15.5557 | -11.3018 | 15.3709 | -87.29 | -49.2908
371 | 0.030917 | -16.568 | 1.3671 | 3.7294 | -0.012477 | -20.2974 | -21904.3793 | 13.0913 | -10.1546 | 46.6333 | 16.0381 | -12.4404 | 15.4273 | -87.1683 | -49.2483
372 | 0.031 | -18.3716 | 1.3547 | 3.0482 | -0.01314 | -21.4198 | -21378.5852 | 14.1556 | -11.7105 | 46.721 | 16.5042 | -13.6535 | 15.4882 | -87.0507 | -49.21
373 | 0.031083 | -20.1305 | 1.3415 | 2.4599 | -0.013789 | -22.5904 | -20832.5266 | 15.1001 | -13.3126 | 46.8117 | 16.9453 | -14.9393 | 15.5538 | -86.9373 | -49.1768
374 | 0.031167 | -21.8431 | 1.3277 | 1.9597 | -0.014412 | -23.8028 | -20266.7402 | 15.923 | -14.9526 | 46.9052 | 17.3515 | -16.2942 | 15.6243 | -86.8282 | -49.1498
375 | 0.03125 | -23.5078 | 1.3133 | 1.5414 | -0.014997 | -25.0492 | -19681.7821 | 16.6225 | -16.6225 | 47.0013 | 17.7125 | -17.7125 | 15.6995 | -86.7234 | -49.1298
376 | 0.031333 | -25.1229 | 1.2983 | 1.1973 | -0.015536 | -26.3202 | -19078.2276 | 17.1978 | -18.3138 | 47.1 | 18.0174 | -19.1866 | 15.7795 | -86.623 | -49.118
377 | 0.031417 | -26.687 | 1.2828 | 0.9187 | -0.016022 | -27.6057 | -18456.6701 | 17.6484 | -20.0182 | 47.201 | 18.256 | -20.7073 | 15.8641 | -86.5271 | -49.1153
378 | 0.0315 | -28.1985 | 1.2668 | 0.69676 | -0.016453 | -28.8953 | -17817.7208 | 17.9744 | -21.7273 | 47.3044 | 18.4186 | -22.2642 | 15.9531 | -86.4358 | -49.1224
379 | 0.031583 | -29.6561 | 1.2503 | 0.52261 | -0.016826 | -30.1787 | -17162.0082 | 18.1765 | -23.4329 | 47.4099 | 18.4968 | -23.8459 | 16.0461 | -86.3491 | -49.1403
380 | 0.031667 | -31.0584 | 1.2335 | 0.3879 | -0.017143 | -31.4463 | -16490.1772 | 18.2557 | -25.1268 | 47.5174 | 18.4837 | -25.4406 | 16.1429 | -86.267 | -49.1695
381 | 0.03175 | -32.4041 | 1.2163 | 0.2851 | -0.017407 | -32.6892 | -15802.8887 | 18.2138 | -26.8008 | 47.6268 | 18.374 | -27.0366 | 16.2431 | -86.1896 | -49.2105
382 | 0.031833 | -33.6918 | 1.1989 | 0.20763 | -0.01762 | -33.8995 | -15100.8188 | 18.053 | -28.447 | 47.738 | 18.1642 | -28.6223 | 16.346 | -86.1169 | -49.2638
383 | 0.031917 | -34.9205 | 1.1813 | 0.14991 | -0.017786 | -35.0704 | -14384.6582 | 17.776 | -30.0575 | 47.8508 | 17.8523 | -30.1866 | 16.4514 | -86.049 | -49.3294
384 | 0.032 | -36.0889 | 1.1635 | 0.10737 | -0.017909 | -36.1963 | -13655.1117 | 17.386 | -31.6249 | 47.9651 | 17.4377 | -31.719 | 16.5587 | -85.9858 | -49.4074
385 | 0.032083 | -37.196 | 1.1456 | 0.076326 | -0.017993 | -37.2723 | -12912.897 | 16.8866 | -33.1419 | 48.0807 | 16.9213 | -33.2099 | 16.6675 | -85.9273 | -49.4978
386 | 0.032167 | -38.2407 | 1.1276 | 0.053879 | -0.01804 | -38.2946 | -12158.7445 | 16.2821 | -34.6012 | 48.1975 | 16.305 | -34.65 | 16.7773 | -85.8737 | -49.6004
387 | 0.03225 | -39.2221 | 1.1096 | 0.037786 | -0.018052 | -39.2599 | -11393.3963 | 15.577 | -35.9963 | 48.3155 | 15.592 | -36.031 | 16.8877 | -85.8248 | -49.7148
388 | 0.032333 | -40.1393 | 1.0915 | 0.02634 | -0.018032 | -40.1657 | -10617.6058 | 14.7763 | -37.3206 | 48.4343 | 14.786 | -37.3451 | 16.9983 | -85.7806 | -49.8409
389 | 0.032417 | -40.9915 | 1.0735 | 0.018258 | -0.017981 | -41.0097 | -9832.1363 | 13.8854 | -38.5681 | 48.554 | 13.8915 | -38.5853 | 17.1088 | -85.7412 | -49.9781
390 | 0.0325 | -41.7778 | 1.0555 | 0.012591 | -0.017901 | -41.7904 | -9037.761 | 12.91 | -39.733 | 48.6744 | 12.9139 | -39.745 | 17.2188 | -85.7066 | -50.1261
391 | 0.032583 | -42.4975 | 1.0376 | 0.0086426 | -0.017792 | -42.5062 | -8235.2618 | 11.8564 | -40.8101 | 48.7954 | 11.8588 | -40.8184 | 17.3281 | -85.6766 | -50.2845
392 | 0.032667 | -43.1501 | 1.0198 | 0.0059074 | -0.017656 | -43.156 | -7425.4284 | 10.731 | -41.7945 | 48.9168 | 10.7325 | -41.8002 | 17.4364 | -85.6514 | -50.4528
393 | 0.03275 | -43.7349 | 1.0022 | 0.0040228 | -0.017493 | -43.7389 | -6609.0581 | 9.5405 | -42.6816 | 49.0385 | 9.5414 | -42.6856 | 17.5436 | -85.6308 | -50.6305
394 | 0.032833 | -44.2515 | 0.98468 | 0.0027307 | -0.017304 | -44.2542 | -5786.9545 | 8.2919 | -43.4676 | 49.1604 | 8.2924 | -43.4703 | 17.6493 | -85.6148 | -50.8173
395 | 0.032917 | -44.6993 | 0.96738 | 0.0018488 | -0.017089 | -44.7011 | -4959.9267 | 6.9925 | -44.149 | 49.2823 | 6.9928 | -44.1508 | 17.7535 | -85.6033 | -51.0126
396 | 0.033 | -45.078 | 0.95029 | 0.0012491 | -0.016849 | -45.0792 | -4128.789 | 5.6498 | -44.7225 | 49.4041 | 5.6499 | -44.7238 | 17.856 | -85.5964 | -51.2162
397 | 0.033083 | -45.3873 | 0.93344 | 0.00084268 | -0.016584 | -45.3882 | -3294.3595 | 4.2713 | -45.1859 | 49.5258 | 4.2714 | -45.1867 | 17.9567 | -85.5939 | -51.4277
398 | 0.033167 | -45.627 | 0.91686 | 0.00056805 | -0.016294 | -45.6276 | -2457.4596 | 2.8649 | -45.537 | 49.6472 | 2.865 | -45.5375 | 18.0554 | -85.5959 | -51.6465
399 | 0.03325 | -45.7968 | 0.90056 | 0.00038287 | -0.015981 | -45.7972 | -1618.9132 | 1.4385 | -45.7742 | 49.7681 | 1.4385 | -45.7746 | 18.1521 | -85.6022 | -51.8725
400 | 0.033333 | -45.8968 | 0.88458 | 0.00025822 | -0.015643 | -45.897 | -779.5458 | 1.0401e-13 | -45.8968 | 49.8885 | 1.0401e-13 | -45.897 | 18.2467 | -85.6129 | -52.1052
401 | 0.033417 | -45.9268 | 0.86894 | 0.00017439 | -0.015282 | -45.9269 | 59.8162 | -1.4426 | -45.9041 | 50.0082 | -1.4426 | -45.9043 | 18.3391 | -85.6277 | -52.3444
402 | 0.0335 | -45.8868 | 0.85366 | 0.00011803 | -0.014898 | -45.887 | 898.3465 | -2.8813 | -45.7963 | 50.1271 | -2.8813 | -45.7964 | 18.4292 | -85.6468 | -52.5896
403 | 0.033583 | -45.7771 | 0.83876 | 8.0124e-05 | -0.014492 | -45.7772 | 1735.2197 | -4.308 | -45.5739 | 50.2452 | -4.308 | -45.574 | 18.5169 | -85.6699 | -52.8407
404 | 0.033667 | -45.5977 | 0.82427 | 5.4606e-05 | -0.014063 | -45.5978 | 2569.6118 | -5.7149 | -45.2382 | 50.3623 | -5.7149 | -45.2382 | 18.6023 | -85.6971 | -53.0972
405 | 0.03375 | -45.3489 | 0.8102 | 3.7395e-05 | -0.013613 | -45.349 | 3400.7015 | -7.0941 | -44.7906 | 50.4782 | -7.0941 | -44.7906 | 18.6852 | -85.7282 | -53.359
406 | 0.033833 | -45.031 | 0.79659 | 2.5759e-05 | -0.013141 | -45.0311 | 4227.6704 | -8.438 | -44.2334 | 50.593 | -8.438 | -44.2334 | 18.7657 | -85.7632 | -53.6258
407 | 0.033917 | -44.6444 | 0.78345 | 1.7864e-05 | -0.012649 | -44.6445 | 5049.7046 | -9.7389 | -43.5693 | 50.7065 | -9.7389 | -43.5693 | 18.8435 | -85.802 | -53.8972
408 | 0.034 | -44.1896 | 0.7708 | 1.2487e-05 | -0.012137 | -44.1896 | 5865.9948 | -10.9895 | -42.8013 | 50.8185 | -10.9895 | -42.8013 | 18.9188 | -85.8445 | -54.1731
409 | 0.034083 | -43.667 | 0.75866 | 8.8071e-06 | -0.011604 | -43.667 | 6675.7373 | -12.1827 | -41.9331 | 50.9291 | -12.1827 | -41.9331 | 18.9915 | -85.8907 | -54.4532
410 | 0.034167 | -43.0772 | 0.74706 | 6.2743e-06 | -0.011053 | -43.0772 | 7478.135 | -13.3116 | -40.9688 | 51.0381 | -13.3116 | -40.9688 | 19.0616 | -85.9404 | -54.7372
411 | 0.03425 | -42.4208 | 0.73601 | 4.5201e-06 | -0.010483 | -42.4208 | 8272.3981 | -14.3695 | -39.9129 | 51.1454 | -14.3695 | -39.9129 | 19.1289 | -85.9935 | -55.025
412 | 0.034333 | -41.6987 | 0.72552 | 3.2967e-06 | -0.0098952 | -41.6987 | 9057.7447 | -15.3503 | -38.7704 | 51.2509 | -15.3503 | -38.7704 | 19.1936 | -86.05 | -55.3162
413 | 0.034417 | -40.9115 | 0.71563 | 2.4371e-06 | -0.0092898 | -40.9115 | 9833.4016 | -16.2479 | -37.5467 | 51.3546 | -16.2479 | -37.5467 | 19.2555 | -86.1099 | -55.6107
414 | 0.0345 | -40.0601 | 0.70634 | 1.8282e-06 | -0.0086677 | -40.0601 | 10598.6054 | -17.0567 | -36.2474 | 51.4564 | -17.0567 | -36.2474 | 19.3146 | -86.1729 | -55.9082
415 | 0.034583 | -39.1453 | 0.69767 | 1.3933e-06 | -0.0080295 | -39.1454 | 11352.6029 | -17.7716 | -34.8788 | 51.5561 | -17.7716 | -34.8788 | 19.3709 | -86.239 | -56.2086
416 | 0.034667 | -38.1683 | 0.68964 | 1.0801e-06 | -0.0073758 | -38.1683 | 12094.652 | -18.3877 | -33.4471 | 51.6537 | -18.3877 | -33.4471 | 19.4245 | -86.3081 | -56.5116
417 | 0.03475 | -37.1299 | 0.68226 | 8.5255e-07 | -0.0067072 | -37.1299 | 12824.0222 | -18.9007 | -31.9593 | 51.7491 | -18.9007 | -31.9593 | 19.4752 | -86.3801 | -56.8169
418 | 0.034833 | -36.0313 | 0.67556 | 6.8601e-07 | -0.0060245 | -36.0313 | 13539.9956 | -19.3066 | -30.4223 | 51.8423 | -19.3066 | -30.4223 | 19.523 | -86.455 | -57.1245
419 | 0.034917 | -34.8737 | 0.66953 | 5.633e-07 | -0.0053283 | -34.8737 | 14241.8678 | -19.6019 | -28.8433 | 51.9332 | -19.6019 | -28.8433 | 19.568 | -86.5326 | -57.4341
420 | 0.035 | -33.6581 | 0.6642 | 4.725e-07 | -0.0046193 | -33.6581 | 14928.9478 | -19.7837 | -27.23 | 52.0217 | -19.7837 | -27.23 | 19.6102 | -86.6128 | -57.7455
421 | 0.035083 | -32.3859 | 0.65959 | 4.0525e-07 | -0.0038983 | -32.3859 | 15600.5597 | -19.8496 | -25.5899 | 52.1078 | -19.8496 | -25.5899 | 19.6494 | -86.6955 | -58.0586
422 | 0.035167 | -31.0585 | 0.65569 | 3.557e-07 | -0.0031661 | -31.0585 | 16256.0425 | -19.7974 | -23.9309 | 52.1913 | -19.7974 | -23.9309 | 19.6858 | -86.7807 | -58.373
423 | 0.03525 | -29.677 | 0.65252 | 3.1977e-07 | -0.0024232 | -29.677 | 16894.7512 | -19.6258 | -22.2611 | 52.2723 | -19.6258 | -22.2611 | 19.7192 | -86.8682 | -58.6887
424 | 0.035333 | -28.2431 | 0.6501 | 2.9464e-07 | -0.0016706 | -28.2431 | 17516.0574 | -19.3338 | -20.5884 | 52.3506 | -19.3338 | -20.5884 | 19.7498 | -86.958 | -59.0055
425 | 0.035417 | -26.7582 | 0.64843 | 2.7842e-07 | -0.00090889 | -26.7582 | 18119.3499 | -18.9209 | -18.9209 | 52.4263 | -18.9209 | -18.9209 | 19.7774 | -87.0499 | -59.3231
426 | 0.0355 | -25.2238 | 0.64752 | 2.6996e-07 | -0.00013892 | -25.2238 | 18704.0352 | -18.3873 | -17.2669 | 52.4993 | -18.3873 | -17.2669 | 19.8022 | -87.1438 | -59.6414
427 | 0.035583 | -23.6414 | 0.64738 | 2.6869e-07 | 0.00063854 | -23.6414 | 19269.5383 | -17.7337 | -15.6343 | 52.5694 | -17.7337 | -15.6343 | 19.824 | -87.2397 | -59.9602
428 | 0.035667 | -22.0127 | 0.64802 | 2.7458e-07 | 0.0014227 | -22.0127 | 19815.3028 | -16.9611 | -14.0314 | 52.6368 | -16.9611 | -14.0314 | 19.8429 | -87.3375 | -60.2793
429 | 0.03575 | -20.3394 | 0.64944 | 2.8816e-07 | 0.0022128 | -20.3394 | 20340.7921 | -16.0713 | -12.4662 | 52.7013 | -16.0713 | -12.4662 | 19.8589 | -87.437 | -60.5986
430 | 0.035833 | -18.6232 | 0.65165 | 3.1055e-07 | 0.003008 | -18.6232 | 20845.4894 | -15.0665 | -10.9464 | 52.7628 | -15.0665 | -10.9464 | 19.8721 | -87.5381 | -60.9178
431 | 0.035917 | -16.8658 | 0.65466 | 3.4366e-07 | 0.0038075 | -16.8658 | 21328.8987 | -13.9493 | -9.48 | 52.8215 | -13.9493 | -9.48 | 19.8823 | -87.6408 | -61.2368
432 | 0.036 | -15.069 | 0.65847 | 3.9042e-07 | 0.0046105 | -15.069 | 21790.5446 | -12.7231 | -8.0744 | 52.8772 | -12.7231 | -8.0744 | 19.8896 | -87.745 | -61.5554
433 | 0.036083 | -13.2346 | 0.66308 | 4.552e-07 | 0.0054163 | -13.2346 | 22229.9735 | -11.3916 | -6.737 | 52.9298 | -11.3916 | -6.737 | 19.8941 | -87.8505 | -61.8733
434 | 0.036167 | -11.3646 | 0.6685 | 5.4442e-07 | 0.0062239 | -11.3646 | 22646.7535 | -9.9589 | -5.4749 | 52.9795 | -9.9589 | -5.4749 | 19.8957 | -87.9572 | -62.1904
435 | 0.03625 | -9.4608 | 0.67472 | 6.6753e-07 | 0.0070325 | -9.4608 | 23040.4752 | -8.4296 | -4.2951 | 53.026 | -8.4296 | -4.2951 | 19.8944 | -88.0651 | -62.5064
436 | 0.036333 | -7.5252 | 0.68175 | 8.3858e-07 | 0.0078414 | -7.5252 | 23410.7519 | -6.809 | -3.2041 | 53.0695 | -6.809 | -3.2041 | 19.8904 | -88.1741 | -62.8212
437 | 0.036417 | -5.5597 | 0.68959 | 1.0785e-06 | 0.0086498 | -5.5597 | 23757.2201 | -5.1024 | -2.208 | 53.1099 | -5.1024 | -2.208 | 19.8835 | -88.284 | -63.1344
438 | 0.0365 | -3.5663 | 0.69824 | 1.4188e-06 | 0.0094567 | -3.5663 | 24079.5396 | -3.3159 | -1.3128 | 53.1472 | -3.3159 | -1.3128 | 19.8738 | -88.3949 | -63.4457
439 | 0.036583 | -1.5471 | 0.7077 | 1.9074e-06 | 0.010261 | -1.5471 | 24377.3942 | -1.4556 | -0.52406 | 53.1813 | -1.4556 | -0.52406 | 19.8614 | -88.5064 | -63.7548
440 | 0.036667 | 0.49591 | 0.71796 | 2.6181e-06 | 0.011063 | 0.49591 | 24650.4918 | 0.47164 | 0.15325 | 53.2123 | 0.47164 | 0.15324 | 19.8463 | -88.6187 | -64.0613
441 | 0.03675 | 2.5606 | 0.72902 | 3.6651e-06 | 0.011861 | 2.5606 | 24898.5647 | 2.459 | 0.71439 | 53.2402 | 2.459 | 0.71439 | 19.8286 | -88.7315 | -64.3646
442 | 0.036833 | 4.645 | 0.74089 | 5.2274e-06 | 0.012654 | 4.645 | 25121.3699 | 4.499 | 1.1552 | 53.2648 | 4.499 | 1.1552 | 19.8083 | -88.8448 | -64.664
443 | 0.036917 | 6.7468 | 0.75354 | 7.5876e-06 | 0.013442 | 6.7468 | 25318.6893 | 6.5843 | 1.4718 | 53.2864 | 6.5843 | 1.4718 | 19.7855 | -88.9585 | -64.9588
444 | 0.037 | 8.864 | 0.76698 | 1.1195e-05 | 0.014224 | 8.864 | 25490.3301 | 8.707 | 1.661 | 53.3047 | 8.707 | 1.661 | 19.7605 | -89.0725 | -65.2478
445 | 0.037083 | 10.9945 | 0.78121 | 1.6773e-05 | 0.014998 | 10.9945 | 25636.1246 | 10.8591 | 1.7199 | 53.3199 | 10.8591 | 1.7199 | 19.7334 | -89.1866 | -65.5296
446 | 0.037167 | 13.136 | 0.7962 | 2.5486e-05 | 0.015765 | 13.136 | 25755.9308 | 13.0324 | 1.6464 | 53.3319 | 13.0324 | 1.6464 | 19.7044 | -89.3009 | -65.8023
447 | 0.03725 | 15.2864 | 0.81197 | 3.9232e-05 | 0.016523 | 15.2864 | 25849.6322 | 15.2186 | 1.4386 | 53.3407 | 15.2185 | 1.4386 | 19.6741 | -89.4152 | -66.0637
448 | 0.037333 | 17.4435 | 0.82849 | 6.1111e-05 | 0.017272 | 17.4435 | 25917.1382 | 17.4091 | 1.0953 | 53.3465 | 17.4091 | 1.0953 | 19.6429 | -89.5294 | -66.3108
449 | 0.037417 | 19.6052 | 0.84577 | 9.6219e-05 | 0.018011 | 19.6051 | 25958.3839 | 19.5955 | 0.61581 | 53.349 | 19.5954 | 0.61581 | 19.6115 | -89.6434 | -66.5403
450 | 0.0375 | 21.7692 | 0.86378 | 0.00015296 | 0.018739 | 21.7691 | 25973.3304 | 21.7692 | 5.0667e-14 | 53.3485 | 21.7691 | 5.0666e-14 | 19.5808 | -89.7572 | -66.7481
451 | 0.037583 | 23.9334 | 0.88252 | 0.00024527 | 0.019455 | 23.9331 | 25961.9648 | 23.9216 | -0.75177 | 53.3448 | 23.9213 | -0.75176 | 19.5518 | -89.8706 | -66.9302
452 | 0.037667 | 26.0955 | 0.90197 | 0.00039627 | 0.020158 | 26.0951 | 25924.3 | 26.044 | -1.6385 | 53.3381 | 26.0436 | -1.6385 | 19.5259 | -89.9835 | -67.0822
453 | 0.03775 | 28.2534 | 0.92213 | 0.00064442 | 0.020849 | 28.2527 | 25860.375 | 28.128 | -2.6589 | 53.3282 | 28.1273 | -2.6588 | 19.5043 | -90.0959 | -67.2001
454 | 0.037833 | 30.4048 | 0.94298 | 0.0010539 | 0.021525 | 30.4038 | 25770.2546 | 30.1651 | -3.8107 | 53.3154 | 30.164 | -3.8106 | 19.4885 | -90.2077 | -67.2806
455 | 0.037917 | 32.5477 | 0.9645 | 0.0017315 | 0.022186 | 32.5459 | 25654.0296 | 32.147 | -5.0916 | 53.2995 | 32.1452 | -5.0913 | 19.4801 | -90.3188 | -67.3208
456 | 0.038 | 34.6798 | 0.98669 | 0.0028557 | 0.02283 | 34.6769 | 25511.8163 | 34.0655 | -6.4983 | 53.2806 | 34.0627 | -6.4978 | 19.4805 | -90.429 | -67.3189
457 | 0.038083 | 36.7989 | 1.0095 | 0.0047235 | 0.023456 | 36.7942 | 25343.757 | 35.9127 | -8.0274 | 53.2588 | 35.9081 | -8.0264 | 19.4913 | -90.5384 | -67.2741
458 | 0.038167 | 38.903 | 1.033 | 0.0078293 | 0.024063 | 38.8952 | 25150.0191 | 37.6808 | -9.6748 | 53.234 | 37.6732 | -9.6728 | 19.5139 | -90.6468 | -67.1865
459 | 0.03825 | 40.9899 | 1.057 | 0.012994 | 0.024645 | 40.9769 | 24930.7957 | 39.3623 | -11.4358 | 53.2064 | 39.3499 | -11.4322 | 19.5497 | -90.7541 | -67.057
460 | 0.038333 | 43.0574 | 1.0817 | 0.021575 | 0.0252 | 43.0359 | 24686.3048 | 40.9501 | -13.3055 | 53.1759 | 40.9295 | -13.2988 | 19.6001 | -90.8603 | -66.8875
461 | 0.038417 | 45.1036 | 1.1069 | 0.035809 | 0.02572 | 45.0678 | 24416.7895 | 42.4371 | -15.2783 | 53.1426 | 42.4034 | -15.2662 | 19.6663 | -90.9652 | -66.6806
462 | 0.0385 | 47.1262 | 1.1326 | 0.059356 | 0.026193 | 47.0669 | 24122.5174 | 43.8168 | -17.3483 | 53.1065 | 43.7617 | -17.3265 | 19.7492 | -91.0689 | -66.4397
463 | 0.038583 | 49.1233 | 1.1588 | 0.098154 | 0.026602 | 49.0252 | 23803.7807 | 45.0831 | -19.5092 | 53.0677 | 44.9931 | -19.4702 | 19.85 | -91.1711 | -66.1688
464 | 0.038667 | 51.0928 | 1.1854 | 0.16172 | 0.02692 | 50.9311 | 23460.8957 | 46.2302 | -21.7543 | 53.0262 | 46.0839 | -21.6854 | 19.9693 | -91.2719 | -65.8723
465 | 0.03875 | 53.0328 | 1.2123 | 0.26505 | 0.027107 | 52.7678 | 23094.2024 | 47.2526 | -24.0764 | 52.9821 | 47.0164 | -23.9561 | 20.1076 | -91.3711 | -65.5552
466 | 0.038833 | 54.9412 | 1.2394 | 0.43113 | 0.027107 | 54.5101 | 22704.0645 | 48.1454 | -26.4681 | 52.9353 | 47.7676 | -26.2604 | 20.2652 | -91.4687 | -65.2231
467 | 0.038917 | 56.8162 | 1.2665 | 0.69394 | 0.026845 | 56.1222 | 22290.8687 | 48.9041 | -28.9218 | 52.8861 | 48.3068 | -28.5685 | 20.4421 | -91.5645 | -64.8815
468 | 0.039 | 58.6557 | 1.2934 | 1.1008 | 0.02624 | 57.5549 | 21855.0245 | 49.5247 | -31.4293 | 52.8344 | 48.5952 | -30.8395 | 20.6375 | -91.6586 | -64.5368
469 | 0.039083 | 60.4581 | 1.3196 | 1.7125 | 0.025221 | 58.7456 | 21396.9637 | 50.0037 | -33.9825 | 52.7802 | 48.5873 | -33.0199 | 20.8504 | -91.7509 | -64.195
470 | 0.039167 | 62.2213 | 1.3448 | 2.5972 | 0.023765 | 59.6241 | 20917.14 | 50.3381 | -36.5728 | 52.7237 | 48.2369 | -35.0461 | 21.079 | -91.8411 | -63.8624
471 | 0.03925 | 63.9437 | 1.3686 | 3.8184 | 0.021927 | 60.1253 | 20416.0287 | 50.5254 | -39.1915 | 52.6649 | 47.5083 | -36.8512 | 21.3208 | -91.9294 | -63.545
472 | 0.039333 | 65.6234 | 1.3905 | 5.4168 | 0.019842 | 60.2066 | 19894.126 | 50.5637 | -41.8299 | 52.6039 | 46.39 | -38.3771 | 21.573 | -92.0156 | -63.2479
473 | 0.039417 | 67.2588 | 1.4104 | 7.3981 | 0.017683 | 59.8607 | 19351.9486 | 50.4516 | -44.479 | 52.5407 | 44.9022 | -39.5866 | 21.8325 | -92.0997 | -62.9752
474 | 0.0395 | 68.8482 | 1.4281 | 9.7312 | 0.015603 | 59.1169 | 18790.0332 | 50.1882 | -47.1298 | 52.4753 | 43.0944 | -40.4683 | 22.0961 | -92.1815 | -62.7296
475 | 0.039583 | 70.3899 | 1.4437 | 12.3593 | 0.013702 | 58.0306 | 18208.9362 | 49.7732 | -49.7732 | 52.4079 | 41.0338 | -41.0338 | 22.361 | -92.2611 | -62.5127
476 | 0.039667 | 71.8825 | 1.4574 | 15.2143 | 0.012024 | 56.6681 | 17609.2325 | 49.2069 | -52.4001 | 52.3386 | 38.792 | -41.3093 | 22.6248 | -92.3383 | -62.3249
477 | 0.03975 | 73.3243 | 1.4694 | 18.2288 | 0.010571 | 55.0955 | 16991.5158 | 48.4902 | -55.0014 | 52.2673 | 36.4353 | -41.3277 | 22.8854 | -92.4131 | -62.1656
478 | 0.039833 | 74.7139 | 1.48 | 21.3427 | 0.0093255 | 53.3712 | 16356.3973 | 47.6244 | -57.5681 | 52.1942 | 34.0201 | -41.1232 | 23.1412 | -92.4854 | -62.0337
479 | 0.039917 | 76.0499 | 1.4893 | 24.5055 | 0.0082604 | 51.5444 | 15704.5054 | 46.6115 | -60.0912 | 52.1194 | 31.5919 | -40.728 | 23.3909 | -92.5552 | -61.9277
480 | 0.04 | 77.3309 | 1.4975 | 27.6766 | 0.0073484 | 49.6543 | 15036.4851 | 45.454 | -62.562 | 52.0428 | 29.1861 | -40.1712 | 23.6335 | -92.6224 | -61.8458
481 | 0.040083 | 78.5555 | 1.5049 | 30.8234 | 0.0065642 | 47.7321 | 14352.9973 | 44.1548 | -64.9718 | 51.9647 | 26.8294 | -39.4783 | 23.8682 | -92.6869 | -61.7861
482 | 0.040167 | 79.7226 | 1.5115 | 33.9208 | 0.0058862 | 45.8018 | 13654.7183 | 42.7175 | -67.312 | 51.885 | 24.5418 | -38.6718 | 24.0946 | -92.7488 | -61.7467
483 | 0.04025 | 80.8309 | 1.5173 | 36.949 | 0.0052963 | 43.882 | 12942.3387 | 41.1463 | -69.5746 | 51.8039 | 22.3377 | -37.771 | 24.3122 | -92.8078 | -61.7257
484 | 0.040333 | 81.8793 | 1.5226 | 39.8928 | 0.0047799 | 41.9865 | 12216.5632 | 39.4457 | -71.7514 | 51.7214 | 20.2272 | -36.7931 | 24.5209 | -92.8641 | -61.7212
485 | 0.040417 | 82.8667 | 1.5274 | 42.7407 | 0.0043249 | 40.126 | 11478.1096 | 37.6207 | -73.8348 | 51.6376 | 18.2168 | -35.7525 | 24.7205 | -92.9175 | -61.7315
486 | 0.0405 | 83.792 | 1.5317 | 45.4838 | 0.0039215 | 38.3082 | 10727.7085 | 35.6769 | -75.8173 | 51.5526 | 16.3108 | -34.6623 | 24.9109 | -92.968 | -61.755
487 | 0.040583 | 84.6543 | 1.5357 | 48.1157 | 0.0035615 | 36.5387 | 9966.1019 | 33.6203 | -77.6919 | 51.4665 | 14.5113 | -33.5335 | 25.0923 | -93.0155 | -61.7901
488 | 0.040667 | 85.4527 | 1.5392 | 50.6313 | 0.0032385 | 34.8214 | 9194.0431 | 31.4572 | -79.4519 | 51.3793 | 12.8186 | -32.3761 | 25.2648 | -93.06 | -61.8355
489 | 0.04075 | 86.1864 | 1.5425 | 53.0275 | 0.0029471 | 33.1589 | 8412.2957 | 29.1946 | -81.0911 | 51.2912 | 11.2322 | -31.1986 | 25.4284 | -93.1016 | -61.8897
490 | 0.040833 | 86.8545 | 1.5454 | 55.3017 | 0.0026827 | 31.5528 | 7621.6327 | 26.8395 | -82.6036 | 51.2022 | 9.7504 | -30.0085 | 25.5835 | -93.14 | -61.9516
491 | 0.040917 | 87.4564 | 1.5481 | 57.4526 | 0.0024417 | 30.0038 | 6822.836 | 24.3996 | -83.9839 | 51.1125 | 8.3708 | -28.8125 | 25.7301 | -93.1753 | -62.0201
492 | 0.041 | 87.9915 | 1.5505 | 59.4795 | 0.0022208 | 28.5119 | 6016.6955 | 21.8826 | -85.2271 | 51.022 | 7.0906 | -27.6162 | 25.8687 | -93.2075 | -62.0942
493 | 0.041083 | 88.459 | 1.5528 | 61.3822 | 0.0020176 | 27.0768 | 5204.0084 | 19.2967 | -86.3287 | 50.931 | 5.9066 | -26.4247 | 25.9993 | -93.2365 | -62.173
494 | 0.041167 | 88.8586 | 1.5548 | 63.161 | 0.0018297 | 25.6976 | 4385.5784 | 16.6504 | -87.2847 | 50.8394 | 4.8153 | -25.2425 | 26.1224 | -93.2623 | -62.2556
495 | 0.04125 | 89.1898 | 1.5566 | 64.8166 | 0.0016552 | 24.3732 | 3562.2146 | 13.9524 | -88.0918 | 50.7474 | 3.8128 | -24.0732 | 26.2381 | -93.2849 | -62.3413
496 | 0.041333 | 89.4522 | 1.5583 | 66.3499 | 0.0014925 | 23.1023 | 2734.7313 | 11.2113 | -88.7469 | 50.6551 | 2.8955 | -22.9202 | 26.3468 | -93.3042 | -62.4295
497 | 0.041417 | 89.6455 | 1.5598 | 67.7622 | 0.0013403 | 21.8833 | 1903.9467 | 8.4364 | -89.2477 | 50.5625 | 2.0594 | -21.7862 | 26.4487 | -93.3202 | -62.5195
498 | 0.0415 | 89.7695 | 1.5611 | 69.0548 | 0.0011972 | 20.7147 | 1070.6821 | 5.6367 | -89.5923 | 50.4698 | 1.3007 | -20.6738 | 26.5442 | -93.333 | -62.6107
499 | 0.041583 | 89.8239 | 1.5623 | 70.2293 | 0.0010623 | 19.5946 | 235.7615 | 2.8214 | -89.7796 | 50.377 | 0.61548 | -19.5849 | 26.6335 | -93.3425 | -62.7027
500 | 0.041667 | 89.8088 | 1.5634 | 71.2874 | 0.00093459 | 18.5213 | -599.9895 | 2.1452e-13 | -89.8088 | 50.2842 | 4.4242e-14 | -18.5213 | 26.717 | -93.3487 | -62.795
501 | 0.04175 | 89.7239 | 1.5643 | 72.2309 | 0.00081328 | 17.493 | -1435.7446 | -2.8183 | -89.6797 | 50.1916 | -0.54947 | -17.4844 | 26.7948 | -93.3515 | -62.8872
502 | 0.041833 | 89.5695 | 1.5651 | 73.0616 | 0.00069766 | 16.5079 | -2270.6775 | -5.6241 | -89.3927 | 50.0991 | -1.0365 | -16.4753 | 26.8673 | -93.3511 | -62.979
503 | 0.041917 | 89.3455 | 1.5658 | 73.7815 | 0.00058708 | 15.5641 | -3103.9626 | -8.4082 | -88.949 | 50.007 | -1.4647 | -15.495 | 26.9347 | -93.3473 | -63.07
504 | 0.042 | 89.0522 | 1.5664 | 74.3925 | 0.00048097 | 14.6598 | -3934.7761 | -11.1612 | -88.35 | 49.9152 | -1.8374 | -14.5442 | 26.9973 | -93.3402 | -63.1601
505 | 0.042083 | 88.6898 | 1.5669 | 74.8966 | 0.00037884 | 13.7932 | -4762.2964 | -13.8741 | -87.5979 | 49.824 | -2.1577 | -13.6234 | 27.0554 | -93.3298 | -63.2488
506 | 0.042167 | 88.2586 | 1.5672 | 75.296 | 0.00028021 | 12.9626 | -5585.7054 | -16.538 | -86.6953 | 49.7333 | -2.4289 | -12.733 | 27.1091 | -93.3161 | -63.3361
507 | 0.04225 | 87.759 | 1.5675 | 75.5928 | 0.00018468 | 12.1663 | -6404.1889 | -19.144 | -85.6455 | 49.6432 | -2.654 | -11.8733 | 27.1588 | -93.2991 | -63.4217
508 | 0.042333 | 87.1914 | 1.5677 | 75.7889 | 9.1871e-05 | 11.4025 | -7216.9376 | -21.6836 | -84.4521 | 49.5539 | -2.8357 | -11.0443 | 27.2046 | -93.2789 | -63.5055
509 | 0.042417 | 86.5564 | 1.5678 | 75.8867 | 1.4358e-06 | 10.6697 | -8023.148 | -24.1485 | -83.1195 | 49.4655 | -2.9767 | -10.246 | 27.2468 | -93.2554 | -63.5873
510 | 0.0425 | 85.8544 | 1.5678 | 75.8882 | -8.6943e-05 | 9.9662 | -8822.0229 | -26.5305 | -81.6524 | 49.3779 | -3.0797 | -9.4784 | 27.2856 | -93.2286 | -63.667
511 | 0.042583 | 85.0863 | 1.5677 | 75.7957 | -0.00017356 | 9.2906 | -9612.7723 | -28.8219 | -80.056 | 49.2914 | -3.1471 | -8.7413 | 27.3211 | -93.1987 | -63.7445
512 | 0.042667 | 84.2526 | 1.5675 | 75.6113 | -0.00025868 | 8.6412 | -10394.6143 | -31.0154 | -78.336 | 49.206 | -3.1811 | -8.0344 | 27.3537 | -93.1656 | -63.8197
513 | 0.04275 | 83.3541 | 1.5673 | 75.3373 | -0.00034258 | 8.0168 | -11166.7759 | -33.1039 | -76.4986 | 49.1217 | -3.1839 | -7.3575 | 27.3834 | -93.1294 | -63.8927
514 | 0.042833 | 82.3917 | 1.5669 | 74.9758 | -0.00042548 | 7.4159 | -11928.4935 | -35.0807 | -74.5503 | 49.0387 | -3.1575 | -6.7101 | 27.4104 | -93.09 | -63.9632
515 | 0.042917 | 81.3663 | 1.5665 | 74.5292 | -0.00050762 | 6.8371 | -12679.014 | -36.9395 | -72.4979 | 48.957 | -3.104 | -6.0919 | 27.435 | -93.0476 | -64.0313
516 | 0.043 | 80.2789 | 1.566 | 73.9997 | -0.00058921 | 6.2792 | -13417.595 | -38.6746 | -70.3489 | 48.8768 | -3.025 | -5.5025 | 27.4572 | -93.0023 | -64.0969
517 | 0.043083 | 79.1304 | 1.5654 | 73.3896 | -0.00067048 | 5.7408 | -14143.5063 | -40.2807 | -68.1109 | 48.7981 | -2.9223 | -4.9414 | 27.4772 | -92.9539 | -64.16
518 | 0.043167 | 77.922 | 1.5647 | 72.7011 | -0.00075163 | 5.2209 | -14856.0299 | -41.7527 | -65.7917 | 48.7209 | -2.7975 | -4.4081 | 27.4953 | -92.9027 | -64.2206
519 | 0.04325 | 76.6548 | 1.564 | 71.9367 | -0.00083286 | 4.7181 | -15554.4611 | -43.0864 | -63.3997 | 48.6454 | -2.652 | -3.9022 | 27.5114 | -92.8486 | -64.2788
520 | 0.043333 | 75.33 | 1.5632 | 71.0986 | -0.00091437 | 4.2314 | -16238.1093 | -44.2779 | -60.9433 | 48.5715 | -2.4871 | -3.4232 | 27.5258 | -92.7917 | -64.3344
521 | 0.043417 | 73.9489 | 1.5622 | 70.1893 | -0.00099636 | 3.7596 | -16906.2983 | -45.3238 | -58.4311 | 48.4995 | -2.3043 | -2.9707 | 27.5386 | -92.7321 | -64.3875
522 | 0.0435 | 72.5127 | 1.5613 | 69.211 | -0.001079 | 3.3017 | -17558.3671 | -46.2214 | -55.872 | 48.4294 | -2.1046 | -2.544 | 27.5498 | -92.6698 | -64.4382
523 | 0.043583 | 71.0229 | 1.5602 | 68.1663 | -0.0011626 | 2.8567 | -18193.6708 | -46.9683 | -53.2751 | 48.3612 | -1.8891 | -2.1428 | 27.5597 | -92.605 | -64.4864
524 | 0.043667 | 69.4809 | 1.559 | 67.0575 | -0.0012473 | 2.4235 | -18811.5809 | -47.563 | -50.6494 | 48.2949 | -1.659 | -1.7666 | 27.5683 | -92.5376 | -64.5322
525 | 0.04375 | 67.8882 | 1.5578 | 65.8871 | -0.0013332 | 2.0011 | -19411.4862 | -48.0042 | -48.0042 | 48.2308 | -1.415 | -1.415 | 27.5757 | -92.4678 | -64.5755
526 | 0.043833 | 66.2462 | 1.5564 | 64.6576 | -0.0014207 | 1.5886 | -19992.7931 | -48.2914 | -45.3486 | 48.1687 | -1.1581 | -1.0875 | 27.582 | -92.3956 | -64.6165
527 | 0.043917 | 64.5566 | 1.555 | 63.3715 | -0.00151 | 1.1851 | -20554.9266 | -48.4246 | -42.692 | 48.1088 | -0.88894 | -0.78371 | 27.5874 | -92.3212 | -64.6551
528 | 0.044 | 62.8209 | 1.5535 | 62.0314 | -0.0016013 | 0.78954 | -21097.3304 | -48.4044 | -40.0436 | 48.0512 | -0.60835 | -0.50327 | 27.5918 | -92.2446 | -64.6915
529 | 0.044083 | 61.0409 | 1.5519 | 60.6398 | -0.0016948 | 0.40108 | -21619.4677 | -48.2318 | -37.4124 | 47.9958 | -0.31691 | -0.24582 | 27.5955 | -92.1659 | -64.7255
530 | 0.044167 | 59.2183 | 1.5502 | 59.1995 | -0.0017909 | 0.018784 | -22120.8219 | -47.9086 | -34.8076 | 47.9428 | -0.015197 | -0.011041 | 27.5984 | -92.0852 | -64.7572
531 | 0.04425 | 57.3547 | 1.5484 | 57.713 | -0.0018899 | -0.35824 | -22600.8967 | -47.437 | -32.2381 | 47.8921 | 0.2963 | 0.20136 | 27.6006 | -92.0025 | -64.7868
532 | 0.044333 | 55.4521 | 1.5465 | 56.183 | -0.001992 | -0.73092 | -23059.2169 | -46.8197 | -29.7127 | 47.8439 | 0.61713 | 0.39165 | 27.6023 | -91.9181 | -64.8141
533 | 0.044417 | 53.5121 | 1.5445 | 54.6123 | -0.0020976 | -1.1001 | -23495.3287 | -46.0601 | -27.2399 | 47.7981 | 0.94694 | 0.56002 | 27.6034 | -91.8319 | -64.8393
534 | 0.0445 | 51.5368 | 1.5424 | 53.0036 | -0.0022071 | -1.4669 | -23908.8004 | -45.162 | -24.828 | 47.7549 | 1.2854 | 0.70666 | 27.6041 | -91.7442 | -64.8623
535 | 0.044583 | 49.528 | 1.5402 | 51.3599 | -0.0023208 | -1.832 | -24299.2224 | -44.1297 | -22.4852 | 47.7141 | 1.6323 | 0.8317 | 27.6045 | -91.6549 | -64.8833
536 | 0.044667 | 47.4876 | 1.5379 | 49.684 | -0.0024393 | -2.1965 | -24666.208 | -42.968 | -20.2192 | 47.676 | 1.9874 | 0.9352 | 27.6045 | -91.5642 | -64.9021
537 | 0.04475 | 45.4176 | 1.5355 | 47.9789 | -0.002563 | -2.5613 | -25009.3937 | -41.6822 | -18.0375 | 47.6405 | 2.3506 | 1.0172 | 27.6042 | -91.4723 | -64.919
538 | 0.044833 | 43.32 | 1.5329 | 46.2475 | -0.0026925 | -2.9275 | -25328.4393 | -40.2779 | -15.9472 | 47.6076 | 2.7219 | 1.0777 | 27.6038 | -91.3791 | -64.9337
539 | 0.044917 | 41.1969 | 1.5302 | 44.493 | -0.0028283 | -3.2961 | -25623.0286 | -38.7613 | -13.9549 | 47.5773 | 3.1012 | 1.1165 | 27.6032 | -91.2849 | -64.9465
540 | 0.045 | 39.0502 | 1.5274 | 42.7184 | -0.0029712 | -3.6682 | -25892.8694 | -37.1389 | -12.0672 | 47.5497 | 3.4887 | 1.1335 | 27.6026 | -91.1897 | -64.9573
541 | 0.045083 | 36.8821 | 1.5244 | 40.9271 | -0.0031217 | -4.045 | -26137.694 | -35.4176 | -10.2898 | 47.5249 | 3.8844 | 1.1285 | 27.6019 | -91.0937 | -64.9661
542 | 0.045167 | 34.6946 | 1.5213 | 39.1224 | -0.0032809 | -4.4277 | -26357.2594 | -33.6046 | -8.6282 | 47.5027 | 4.2886 | 1.1011 | 27.6013 | -90.9969 | -64.973
543 | 0.04525 | 32.4899 | 1.518 | 37.3076 | -0.0034495 | -4.8177 | -26551.3475 | -31.7074 | -7.0875 | 47.4832 | 4.7016 | 1.0509 | 27.6008 | -90.8996 | -64.9778
544 | 0.045333 | 30.2701 | 1.5146 | 35.4863 | -0.0036286 | -5.2162 | -26719.7654 | -29.7339 | -5.6721 | 47.4665 | 5.1238 | 0.97742 | 27.6004 | -90.8017 | -64.9807
545 | 0.045417 | 28.0373 | 1.5109 | 33.6622 | -0.0038194 | -5.6249 | -26862.3455 | -27.6921 | -4.386 | 47.4525 | 5.5556 | 0.87992 | 27.6003 | -90.7034 | -64.9817
546 | 0.0455 | 25.7938 | 1.5071 | 31.8391 | -0.004023 | -6.0453 | -26978.9456 | -25.5904 | -3.2328 | 47.4413 | 5.9976 | 0.75767 | 27.6005 | -90.6049 | -64.9806
547 | 0.045583 | 23.5416 | 1.5031 | 30.0208 | -0.004241 | -6.4792 | -27069.4494 | -23.4371 | -2.2155 | 47.4327 | 6.4504 | 0.60975 | 27.601 | -90.5062 | -64.9776
548 | 0.045667 | 21.2829 | 1.4988 | 28.2115 | -0.0044749 | -6.9285 | -27133.7661 | -21.2409 | -1.3364 | 47.4269 | 6.9149 | 0.43505 | 27.602 | -90.4074 | -64.9725
549 | 0.04575 | 19.02 | 1.4944 | 26.4154 | -0.0047265 | -7.3954 | -27171.8308 | -19.0106 | -0.59743 | 47.4239 | 7.3918 | 0.2323 | 27.6034 | -90.3087 | -64.9654
550 | 0.045833 | 16.755 | 1.4896 | 24.6371 | -0.0049978 | -7.8821 | -27183.6047 | -16.755 | -4.1048e-14 | 47.4235 | 7.8821 | 1.9311e-14 | 27.6055 | -90.2102 | -64.9563
551 | 0.045917 | 14.4901 | 1.4846 | 22.8813 | -0.005291 | -8.3912 | -27169.0747 | -14.483 | 0.45515 | 47.4258 | 8.387 | -0.26357 | 27.6082 | -90.112 | -64.945
552 | 0.046 | 12.2276 | 1.4794 | 21.1529 | -0.0056086 | -8.9253 | -27128.2539 | -12.2034 | 0.76778 | 47.4308 | 8.9077 | -0.56043 | 27.6118 | -90.0143 | -64.9315
553 | 0.046083 | 9.9695 | 1.4737 | 19.4571 | -0.0059531 | -9.4876 | -27061.181 | -9.9252 | 0.93821 | 47.4385 | 9.4455 | -0.89286 | 27.6162 | -89.917 | -64.9159
554 | 0.046167 | 7.7181 | 1.4678 | 17.7994 | -0.0063274 | -10.0813 | -26967.9211 | -7.6572 | 0.96733 | 47.4488 | 10.0018 | -1.2635 | 27.6217 | -89.8204 | -64.898
555 | 0.04625 | 5.4756 | 1.4615 | 16.1856 | -0.0067346 | -10.71 | -26848.5646 | -5.4081 | 0.85657 | 47.4617 | 10.5782 | -1.6754 | 27.6283 | -89.7245 | -64.8777
556 | 0.046333 | 3.2441 | 1.4547 | 14.6217 | -0.0071777 | -11.3777 | -26703.2282 | -3.1866 | 0.60788 | 47.4772 | 11.1761 | -2.132 | 27.6362 | -89.6294 | -64.8551
557 | 0.046417 | 1.0257 | 1.4476 | 13.1141 | -0.0076599 | -12.0884 | -26532.0538 | -1.001 | 0.22376 | 47.4952 | 11.7973 | -2.637 | 27.6456 | -89.5353 | -64.83
558 | 0.0465 | -1.1772 | 1.4399 | 11.6693 | -0.0081839 | -12.8466 | -26335.2091 | 1.1403 | -0.29277 | 47.5157 | 12.443 | -3.1948 | 27.6566 | -89.4423 | -64.8024
559 | 0.046583 | -3.3628 | 1.4317 | 10.2941 | -0.0087521 | -13.6568 | -26112.8869 | 3.2292 | -0.93818 | 47.5387 | 13.1146 | -3.8101 | 27.6694 | -89.3504 | -64.7722
560 | 0.046667 | -5.5287 | 1.423 | 8.995 | -0.0093661 | -14.5237 | -25865.3054 | 5.2581 | -1.7085 | 47.5642 | 13.8128 | -4.4881 | 27.6843 | -89.2598 | -64.7394
561 | 0.04675 | -7.6729 | 1.4136 | 7.7787 | -0.010026 | -15.4516 | -25592.7074 | 7.2193 | -2.5991 | 47.5921 | 14.5381 | -5.234 | 27.7015 | -89.1705 | -64.704
562 | 0.046833 | -9.7935 | 1.4036 | 6.6512 | -0.01073 | -16.4446 | -25295.3608 | 9.1057 | -3.6052 | 47.6223 | 15.2898 | -6.0537 | 27.7212 | -89.0826 | -64.6659
563 | 0.046917 | -11.8882 | 1.3928 | 5.6179 | -0.011474 | -17.5061 | -24973.5577 | 10.9104 | -4.7214 | 47.6548 | 16.0663 | -6.9525 | 27.7437 | -88.9963 | -64.6252
564 | 0.047 | -13.955 | 1.3814 | 4.6831 | -0.012252 | -18.6382 | -24627.6142 | 12.6269 | -5.9418 | 47.6895 | 16.8643 | -7.9358 | 27.7691 | -88.9116 | -64.582
565 | 0.047083 | -15.9921 | 1.3691 | 3.8496 | -0.013054 | -19.8417 | -24257.8704 | 14.2491 | -7.2603 | 47.7265 | 17.6791 | -9.0079 | 27.7979 | -88.8285 | -64.5365
566 | 0.047167 | -17.9974 | 1.3561 | 3.118 | -0.013867 | -21.1154 | -23864.6901 | 15.7712 | -8.6703 | 47.7656 | 18.5035 | -10.1724 | 27.83 | -88.7473 | -64.4888
567 | 0.04725 | -19.9689 | 1.3422 | 2.4869 | -0.014678 | -22.4559 | -23448.4597 | 17.1881 | -10.165 | 47.8068 | 19.3287 | -11.431 | 27.8659 | -88.6679 | -64.4394
568 | 0.047333 | -21.9048 | 1.3275 | 1.9526 | -0.015469 | -23.8574 | -23009.5889 | 18.4948 | -11.7372 | 47.85 | 20.1435 | -12.7834 | 27.9054 | -88.5905 | -64.3885
569 | 0.047417 | -23.8032 | 1.312 | 1.5087 | -0.016228 | -25.312 | -22548.5094 | 19.6872 | -13.3794 | 47.8952 | 20.935 | -14.2274 | 27.9488 | -88.515 | -64.3368
570 | 0.0475 | -25.6623 | 1.2958 | 1.1474 | -0.016941 | -26.8097 | -22065.6749 | 20.7612 | -15.0839 | 47.9423 | 21.6895 | -15.7583 | 27.996 | -88.4417 | -64.2847
571 | 0.047583 | -27.4802 | 1.2789 | 0.85895 | -0.017599 | -28.3392 | -21561.5607 | 21.7137 | -16.8428 | 47.9913 | 22.3924 | -17.3693 | 28.0469 | -88.3705 | -64.2329
572 | 0.047667 | -29.2553 | 1.2613 | 0.63325 | -0.018197 | -29.8886 | -21036.6629 | 22.5416 | -18.648 | 48.042 | 23.0295 | -19.0517 | 28.1014 | -88.3014 | -64.182
573 | 0.04775 | -30.9858 | 1.2431 | 0.45996 | -0.018732 | -31.4458 | -20491.4982 | 23.2428 | -20.4913 | 48.0945 | 23.5878 | -20.7955 | 28.1591 | -88.2347 | -64.1327
574 | 0.047833 | -32.67 | 1.2243 | 0.32934 | -0.019206 | -32.9994 | -19926.6035 | 23.8154 | -22.3642 | 48.1487 | 24.0555 | -22.5896 | 28.2199 | -88.1702 | -64.0855
575 | 0.047917 | -34.3064 | 1.2051 | 0.23258 | -0.019622 | -34.5389 | -19342.5348 | 24.2583 | -24.2583 | 48.2044 | 24.4227 | -24.4227 | 28.2833 | -88.1081 | -64.0411
576 | 0.048 | -35.8933 | 1.1855 | 0.16208 | -0.019984 | -36.0553 | -18739.8673 | 24.5706 | -26.1651 | 48.2616 | 24.6816 | -26.2832 | 28.349 | -88.0484 | -63.9998
577 | 0.048083 | -37.4292 | 1.1655 | 0.11151 | -0.020297 | -37.5407 | -18119.1944 | 24.7524 | -28.076 | 48.3203 | 24.8261 | -28.1597 | 28.4168 | -87.9912 | -63.9622
578 | 0.048167 | -38.9126 | 1.1452 | 0.075761 | -0.020566 | -38.9884 | -17481.1275 | 24.8038 | -29.9827 | 48.3803 | 24.8521 | -30.0411 | 28.4862 | -87.9365 | -63.9286
579 | 0.04825 | -40.3422 | 1.1247 | 0.050852 | -0.020793 | -40.3931 | -16826.2949 | 24.726 | -31.8766 | 48.4417 | 24.7572 | -31.9168 | 28.5569 | -87.8843 | -63.8991
580 | 0.048333 | -41.7166 | 1.1039 | 0.033729 | -0.020984 | -41.7503 | -16155.3416 | 24.5204 | -33.7494 | 48.5043 | 24.5402 | -33.7767 | 28.6287 | -87.8346 | -63.874
581 | 0.048417 | -43.0344 | 1.0829 | 0.022112 | -0.021141 | -43.0565 | -15468.9285 | 24.1889 | -35.5929 | 48.568 | 24.2013 | -35.6112 | 28.7012 | -87.7876 | -63.8535
582 | 0.0485 | -44.2943 | 1.0618 | 0.014331 | -0.021265 | -44.3086 | -14767.7318 | 23.7341 | -37.3989 | 48.6328 | 23.7418 | -37.411 | 28.7744 | -87.7432 | -63.8375
583 | 0.048583 | -45.4952 | 1.0405 | 0.0091825 | -0.021359 | -45.5044 | -14052.4421 | 23.159 | -39.1597 | 48.6987 | 23.1636 | -39.1676 | 28.848 | -87.7014 | -63.8262
584 | 0.048667 | -46.636 | 1.0191 | 0.0058182 | -0.021423 | -46.6418 | -13323.7642 | 22.4671 | -40.8675 | 48.7654 | 22.4699 | -40.8726 | 28.9218 | -87.6623 | -63.8195
585 | 0.04875 | -47.7155 | 0.9977 | 0.0036459 | -0.02146 | -47.7192 | -12582.4158 | 21.6624 | -42.5148 | 48.833 | 21.6641 | -42.5181 | 28.9956 | -87.6259 | -63.8174
586 | 0.048833 | -48.7328 | 0.97624 | 0.0022597 | -0.021469 | -48.735 | -11829.1274 | 20.7494 | -44.0947 | 48.9014 | 20.7504 | -44.0968 | 29.0694 | -87.5922 | -63.8199
587 | 0.048917 | -49.6867 | 0.95478 | 0.0013855 | -0.021451 | -49.6881 | -11064.6411 | 19.733 | -45.6002 | 48.9705 | 19.7335 | -45.6015 | 29.1431 | -87.5612 | -63.8269
588 | 0.049 | -50.5766 | 0.93332 | 0.0008404 | -0.021406 | -50.5774 | -10289.7101 | 18.6185 | -47.0249 | 49.0402 | 18.6188 | -47.0257 | 29.2165 | -87.5329 | -63.8384
589 | 0.049083 | -51.4014 | 0.91192 | 0.00050443 | -0.021335 | -51.4019 | -9505.0979 | 17.4116 | -48.3626 | 49.1105 | 17.4118 | -48.3631 | 29.2895 | -87.5073 | -63.8543
590 | 0.049167 | -52.1605 | 0.89058 | 0.00029965 | -0.021237 | -52.1608 | -8711.5777 | 16.1185 | -49.6076 | 49.1812 | 16.1186 | -49.6079 | 29.3621 | -87.4844 | -63.8746
591 | 0.04925 | -52.8531 | 0.86935 | 0.0001762 | -0.021114 | -52.8533 | -7909.9313 | 14.7456 | -50.7545 | 49.2524 | 14.7456 | -50.7547 | 29.4342 | -87.4643 | -63.8992
592 | 0.049333 | -53.4786 | 0.84823 | 0.00010259 | -0.020965 | -53.4787 | -7100.9485 | 13.2996 | -51.7985 | 49.3239 | 13.2996 | -51.7986 | 29.5056 | -87.4468 | -63.9279
593 | 0.049417 | -54.0364 | 0.82727 | 5.9152e-05 | -0.020791 | -54.0365 | -6285.4266 | 11.7877 | -52.7351 | 49.3956 | 11.7877 | -52.7351 | 29.5765 | -87.4321 | -63.9608
594 | 0.0495 | -54.526 | 0.80648 | 3.3789e-05 | -0.020591 | -54.5261 | -5464.1691 | 10.2172 | -53.5602 | 49.4675 | 10.2172 | -53.5603 | 29.6466 | -87.42 | -63.9977
595 | 0.049583 | -54.947 | 0.78589 | 1.9128e-05 | -0.020366 | -54.947 | -4637.9853 | 8.5956 | -54.2705 | 49.5395 | 8.5956 | -54.2705 | 29.7158 | -87.4107 | -64.0385
596 | 0.049667 | -55.2989 | 0.76552 | 1.0735e-05 | -0.020116 | -55.2989 | -3807.6893 | 6.9308 | -54.8629 | 49.6115 | 6.9308 | -54.8629 | 29.7843 | -87.4039 | -64.0832
597 | 0.04975 | -55.5815 | 0.7454 | 5.9754e-06 | -0.019842 | -55.5815 | -2974.0993 | 5.2307 | -55.3348 | 49.6835 | 5.2307 | -55.3348 | 29.8518 | -87.3999 | -64.1317
598 | 0.049833 | -55.7945 | 0.72556 | 3.3006e-06 | -0.019543 | -55.7945 | -2138.0368 | 3.5034 | -55.6844 | 49.7554 | 3.5034 | -55.6844 | 29.9183 | -87.3984 | -64.1839
599 | 0.049917 | -55.9378 | 0.70602 | 1.8101e-06 | -0.019221 | -55.9378 | -1300.3255 | 1.757 | -55.9102 | 49.8271 | 1.757 | -55.9102 | 29.9838 | -87.3996 | -64.2397
600 | 0.05 | -56.0112 | 0.6868 | 9.8625e-07 | -0.018875 | -56.0112 | -461.7911 | 2.4015e-13 | -56.0112 | 49.8986 | 2.4015e-13 | -56.0112 | 30.0483 | -87.4033 | -64.2989
601 | 0.050083 | -56.0148 | 0.66792 | 5.3424e-07 | -0.018505 | -56.0148 | 376.7401 | -1.7595 | -55.9871 | 49.9697 | -1.7595 | -55.9871 | 30.1116 | -87.4096 | -64.3616
602 | 0.050167 | -55.9485 | 0.64942 | 2.8793e-07 | -0.018113 | -55.9485 | 1214.4418 | -3.513 | -55.8381 | 50.0404 | -3.513 | -55.8381 | 30.1737 | -87.4184 | -64.4276
603 | 0.05025 | -55.8124 | 0.6313 | 1.5453e-07 | -0.017698 | -55.8124 | 2050.4885 | -5.2524 | -55.5647 | 50.1107 | -5.2524 | -55.5647 | 30.2345 | -87.4296 | -64.4968
604 | 0.050333 | -55.6068 | 0.61361 | 8.2671e-08 | -0.017261 | -55.6068 | 2884.0564 | -6.9694 | -55.1683 | 50.1805 | -6.9694 | -55.1683 | 30.2941 | -87.4433 | -64.5691
605 | 0.050417 | -55.3318 | 0.59635 | 4.413e-08 | -0.016802 | -55.3318 | 3714.3239 | -8.6558 | -54.6506 | 50.2496 | -8.6558 | -54.6506 | 30.3524 | -87.4595 | -64.6445
606 | 0.0505 | -54.9878 | 0.57954 | 2.3533e-08 | -0.016322 | -54.9878 | 4540.4729 | -10.3037 | -54.0139 | 50.3181 | -10.3037 | -54.0139 | 30.4092 | -87.478 | -64.7227
607 | 0.050583 | -54.5752 | 0.56322 | 1.2552e-08 | -0.015821 | -54.5752 | 5361.6892 | -11.9052 | -53.2609 | 50.3859 | -11.9052 | -53.2609 | 30.4647 | -87.4988 | -64.8038
608 | 0.050667 | -54.0944 | 0.5474 | 6.7065e-09 | -0.015301 | -54.0944 | 6177.1636 | -13.4527 | -52.3949 | 50.4529 | -13.4527 | -52.3949 | 30.5187 | -87.5219 | -64.8876
609 | 0.05075 | -53.5459 | 0.5321 | 3.5944e-09 | -0.01476 | -53.5459 | 6986.0926 | -14.9388 | -51.4198 | 50.5191 | -14.9388 | -51.4198 | 30.5712 | -87.5473 | -64.974
610 | 0.050833 | -52.9302 | 0.51734 | 1.9358e-09 | -0.014201 | -52.9302 | 7787.6789 | -16.3563 | -50.3397 | 50.5844 | -16.3563 | -50.3397 | 30.6222 | -87.5749 | -65.063
611 | 0.050917 | -52.2482 | 0.50314 | 1.0494e-09 | -0.013622 | -52.2482 | 8581.1326 | -17.6984 | -49.1593 | 50.6487 | -17.6984 | -49.1593 | 30.6716 | -87.6046 | -65.1544
612 | 0.051 | -51.5003 | 0.48952 | 5.7368e-10 | -0.013026 | -51.5003 | 9365.672 | -18.9585 | -47.8838 | 50.7121 | -18.9585 | -47.8838 | 30.7194 | -87.6364 | -65.248
613 | 0.051083 | -50.6875 | 0.47649 | 3.1694e-10 | -0.012413 | -50.6875 | 10140.5238 | -20.1304 | -46.5187 | 50.7743 | -20.1304 | -46.5187 | 30.7655 | -87.6704 | -65.3439
614 | 0.051167 | -49.8105 | 0.46408 | 1.7733e-10 | -0.011782 | -49.8105 | 10904.9247 | -21.2083 | -45.0699 | 50.8355 | -21.2083 | -45.0699 | 30.81 | -87.7063 | -65.4419
615 | 0.05125 | -48.8703 | 0.4523 | 1.0071e-10 | -0.011136 | -48.8703 | 11658.1213 | -22.1867 | -43.5438 | 50.8955 | -22.1867 | -43.5438 | 30.8528 | -87.7441 | -65.542
616 | 0.051333 | -47.8678 | 0.44116 | 5.8195e-11 | -0.010474 | -47.8678 | 12399.3715 | -23.0605 | -41.9469 | 50.9542 | -23.0605 | -41.9469 | 30.8939 | -87.7839 | -65.6439
617 | 0.051417 | -46.8041 | 0.43069 | 3.4301e-11 | -0.0097975 | -46.8041 | 13127.945 | -23.8252 | -40.2862 | 51.0117 | -23.8252 | -40.2862 | 30.9332 | -87.8256 | -65.7476
618 | 0.0515 | -45.6802 | 0.42089 | 2.0675e-11 | -0.0091067 | -45.6802 | 13843.1238 | -24.4767 | -38.5691 | 51.0679 | -24.4767 | -38.5691 | 30.9708 | -87.869 | -65.8531
619 | 0.051583 | -44.4973 | 0.41178 | 1.2777e-11 | -0.0084025 | -44.4973 | 14544.2034 | -25.0112 | -36.8028 | 51.1228 | -25.0112 | -36.8028 | 31.0066 | -87.9142 | -65.9601
620 | 0.051667 | -43.2566 | 0.40338 | 8.1183e-12 | -0.0076855 | -43.2566 | 15230.493 | -25.4256 | -34.9953 | 51.1762 | -25.4256 | -34.9953 | 31.0405 | -87.9611 | -66.0687
621 | 0.05175 | -41.9593 | 0.39569 | 5.317e-12 | -0.0069565 | -41.9593 | 15901.3165 | -25.7172 | -33.1544 | 51.2282 | -25.7172 | -33.1544 | 31.0726 | -88.0096 | -66.1786
622 | 0.051833 | -40.6068 | 0.38874 | 3.5992e-12 | -0.0062162 | -40.6068 | 16556.0129 | -25.8838 | -31.2881 | 51.2787 | -25.8838 | -31.2881 | 31.1029 | -88.0596 | -66.2898
623 | 0.051917 | -39.2004 | 0.38252 | 2.5246e-12 | -0.0054654 | -39.2004 | 17193.9373 | -25.9237 | -29.4047 | 51.3277 | -25.9237 | -29.4047 | 31.1313 | -88.1112 | -66.4023
624 | 0.052 | -37.7416 | 0.37706 | 1.8394e-12 | -0.0047048 | -37.7416 | 17814.4613 | -25.8359 | -27.5125 | 51.3752 | -25.8359 | -27.5125 | 31.1578 | -88.1643 | -66.5158
625 | 0.052083 | -36.2319 | 0.37235 | 1.3955e-12 | -0.0039352 | -36.2319 | 18416.9736 | -25.6198 | -25.6198 | 51.421 | -25.6198 | -25.6198 | 31.1824 | -88.2187 | -66.6303
626 | 0.052167 | -34.6727 | 0.36842 | 1.1046e-12 | -0.0031573 | -34.6727 | 19000.8808 | -25.2753 | -23.7351 | 51.4652 | -25.2753 | -23.7351 | 31.2052 | -88.2745 | -66.7457
627 | 0.05225 | -33.0656 | 0.36526 | 9.1405e-13 | -0.002372 | -33.0656 | 19565.6077 | -24.8029 | -21.8667 | 51.5078 | -24.8029 | -21.8667 | 31.226 | -88.3316 | -66.8619
628 | 0.052333 | -31.4123 | 0.36289 | 7.9199e-13 | -0.0015799 | -31.4123 | 20110.5981 | -24.2036 | -20.0229 | 51.5487 | -24.2036 | -20.0229 | 31.2449 | -88.3898 | -66.9788
629 | 0.052417 | -29.7144 | 0.36131 | 7.195e-13 | -0.00078198 | -29.7144 | 20635.3153 | -23.479 | -18.2122 | 51.5878 | -23.479 | -18.2122 | 31.2619 | -88.4493 | -67.0962
630 | 0.0525 | -27.9736 | 0.36052 | 6.8601e-13 | 2.1055e-05 | -27.9736 | 21139.2426 | -22.6311 | -16.4425 | 51.6253 | -22.6311 | -16.4425 | 31.2769 | -88.5098 | -67.2142
631 | 0.052583 | -26.1918 | 0.36055 | 6.8689e-13 | 0.00082838 | -26.1918 | 21621.8838 | -21.6627 | -14.722 | 51.6609 | -21.6627 | -14.722 | 31.29 | -88.5713 | -67.3326
632 | 0.052667 | -24.3706 | 0.36137 | 7.2246e-13 | 0.0016392 | -24.3706 | 22082.7637 | -20.5768 | -13.0584 | 51.6948 | -20.5768 | -13.0584 | 31.3012 | -88.6338 | -67.4512
633 | 0.05275 | -22.5119 | 0.36301 | 7.981e-13 | 0.0024527 | -22.5119 | 22521.4285 | -19.377 | -11.4595 | 51.7269 | -19.377 | -11.4595 | 31.3105 | -88.6972 | -67.5701
634 | 0.052833 | -20.6176 | 0.36547 | 9.2554e-13 | 0.003268 | -20.6176 | 22937.4465 | -18.0674 | -9.9326 | 51.7571 | -18.0674 | -9.9326 | 31.3178 | -88.7615 | -67.6891
635 | 0.052917 | -18.6897 | 0.36873 | 1.1258e-12 | 0.0040844 | -18.6897 | 23330.4082 | -16.6526 | -8.4849 | 51.7855 | -16.6526 | -8.4849 | 31.3232 | -88.8265 | -67.808
636 | 0.053 | -16.7299 | 0.37282 | 1.4345e-12 | 0.004901 | -16.7299 | 23699.9269 | -15.1377 | -7.1232 | 51.8121 | -15.1377 | -7.1232 | 31.3267 | -88.8922 | -67.9269
637 | 0.053083 | -14.7403 | 0.37772 | 1.912e-12 | 0.0057171 | -14.7403 | 24045.639 | -13.528 | -5.8541 | 51.8367 | -13.528 | -5.8541 | 31.3283 | -88.9586 | -68.0456
638 | 0.053167 | -12.723 | 0.38344 | 2.6608e-12 | 0.0065317 | -12.723 | 24367.2044 | -11.8295 | -4.6836 | 51.8595 | -11.8295 | -4.6836 | 31.3279 | -89.0256 | -68.164
639 | 0.05325 | -10.6798 | 0.38997 | 3.8584e-12 | 0.0073441 | -10.6798 | 24664.3069 | -10.0484 | -3.6177 | 51.8804 | -10.0484 | -3.6177 | 31.3257 | -89.0931 | -68.2821
640 | 0.053333 | -8.6129 | 0.39731 | 5.8166e-12 | 0.0081534 | -8.6129 | 24936.6543 | -8.1914 | -2.6615 | 51.8993 | -8.1914 | -2.6615 | 31.3216 | -89.1611 | -68.3996
641 | 0.053417 | -6.5244 | 0.40547 | 9.094e-12 | 0.008959 | -6.5244 | 25183.979 | -6.2653 | -1.8202 | 51.9164 | -6.2653 | -1.8202 | 31.3156 | -89.2294 | -68.5166
642 | 0.0535 | -4.4163 | 0.41442 | 1.4708e-11 | 0.0097598 | -4.4163 | 25406.038 | -4.2776 | -1.0983 | 51.9315 | -4.2776 | -1.0983 | 31.3078 | -89.2981 | -68.633
643 | 0.053583 | -2.2908 | 0.42418 | 2.4545e-11 | 0.010555 | -2.2908 | 25602.6131 | -2.2356 | -0.49971 | 51.9447 | -2.2356 | -0.49971 | 31.2981 | -89.3671 | -68.7486
644 | 0.053667 | -0.14991 | 0.43474 | 4.2151e-11 | 0.011344 | -0.14991 | 25773.5116 | -0.14725 | -0.02809 | 51.956 | -0.14725 | -0.02809 | 31.2866 | -89.4363 | -68.8634
645 | 0.05375 | 2.0041 | 0.44608 | 7.429e-11 | 0.012127 | 2.0041 | 25918.5657 | 1.9794 | 0.31351 | 51.9654 | 1.9794 | 0.31351 | 31.2733 | -89.5056 | -68.9773
646 | 0.053833 | 4.1691 | 0.45821 | 1.3403e-10 | 0.012901 | 4.1691 | 26037.6334 | 4.1363 | 0.52253 | 51.9728 | 4.1363 | 0.52253 | 31.2582 | -89.5751 | -69.0901
647 | 0.053917 | 6.343 | 0.47111 | 2.4688e-10 | 0.013667 | 6.343 | 26130.5983 | 6.3148 | 0.59693 | 51.9784 | 6.3148 | 0.59693 | 31.2413 | -89.6445 | -69.2019
648 | 0.054 | 8.5235 | 0.48478 | 4.6314e-10 | 0.014423 | 8.5235 | 26197.3697 | 8.5067 | 0.5352 | 51.982 | 8.5067 | 0.5352 | 31.2228 | -89.7139 | -69.3125
649 | 0.054083 | 10.7085 | 0.4992 | 8.8272e-10 | 0.015169 | 10.7085 | 26237.8827 | 10.7032 | 0.33636 | 51.9837 | 10.7032 | 0.33636 | 31.2024 | -89.7832 | -69.4218
650 | 0.054167 | 12.8958 | 0.51437 | 1.7054e-09 | 0.015905 | 12.8958 | 26252.0984 | 12.8958 | 3.3173e-14 | 51.9835 | 12.8958 | 3.3173e-14 | 31.1804 | -89.8524 | -69.5297
651 | 0.05425 | 15.0831 | 0.53027 | 3.3326e-09 | 0.016628 | 15.0831 | 26240.004 | 15.0757 | -0.47377 | 51.9814 | 15.0757 | -0.47377 | 31.1568 | -89.9213 | -69.6362
652 | 0.054333 | 17.2684 | 0.5469 | 6.5734e-09 | 0.01734 | 17.2684 | 26201.6122 | 17.2343 | -1.0843 | 51.9774 | 17.2343 | -1.0843 | 31.1315 | -89.99 | -69.7412
653 | 0.054417 | 19.4493 | 0.56424 | 1.3062e-08 | 0.018038 | 19.4493 | 26136.9621 | 19.363 | -1.8303 | 51.9716 | 19.363 | -1.8303 | 31.1046 | -90.0583 | -69.8445
654 | 0.0545 | 21.6238 | 0.58228 | 2.6103e-08 | 0.018723 | 21.6238 | 26046.1186 | 21.4533 | -2.7102 | 51.9639 | 21.4533 | -2.7102 | 31.0761 | -90.1262 | -69.9462
655 | 0.054583 | 23.7896 | 0.601 | 5.2368e-08 | 0.019393 | 23.7896 | 25929.1723 | 23.4967 | -3.7215 | 51.9544 | 23.4967 | -3.7215 | 31.0461 | -90.1937 | -70.0461
656 | 0.054667 | 25.9446 | 0.6204 | 1.0532e-07 | 0.020048 | 25.9446 | 25786.2397 | 25.485 | -4.8615 | 51.943 | 25.485 | -4.8615 | 31.0146 | -90.2607 | -70.1441
657 | 0.05475 | 28.0866 | 0.64045 | 2.1202e-07 | 0.020688 | 28.0866 | 25617.4628 | 27.4102 | -6.1269 | 51.9299 | 27.4102 | -6.1269 | 30.9816 | -90.3271 | -70.2402
658 | 0.054833 | 30.2135 | 0.66113 | 4.2669e-07 | 0.021311 | 30.2135 | 25423.0094 | 29.2642 | -7.5138 | 51.915 | 29.2642 | -7.5138 | 30.9471 | -90.3929 | -70.3342
659 | 0.054917 | 32.3231 | 0.68244 | 8.5749e-07 | 0.021917 | 32.3231 | 25203.0722 | 31.0396 | -9.0178 | 51.8984 | 31.0396 | -9.0178 | 30.9113 | -90.458 | -70.4262
660 | 0.055 | 34.4133 | 0.70436 | 1.7189e-06 | 0.022505 | 34.4133 | 24957.8694 | 32.729 | -10.6343 | 51.88 | 32.729 | -10.6343 | 30.8742 | -90.5223 | -70.5158
661 | 0.055083 | 36.482 | 0.72686 | 3.4336e-06 | 0.023075 | 36.482 | 24687.644 | 34.3252 | -12.3578 | 51.8599 | 34.3252 | -12.3578 | 30.8358 | -90.5859 | -70.6032
662 | 0.055167 | 38.5272 | 0.74994 | 6.8288e-06 | 0.023626 | 38.5272 | 24392.6638 | 35.8217 | -14.1828 | 51.8381 | 35.8217 | -14.1828 | 30.7962 | -90.6486 | -70.6879
663 | 0.05525 | 40.5468 | 0.77357 | 1.3512e-05 | 0.024158 | 40.5468 | 24073.2208 | 37.212 | -16.1031 | 51.8147 | 37.212 | -16.1031 | 30.7556 | -90.7105 | -70.77
664 | 0.055333 | 42.5387 | 0.79772 | 2.6578e-05 | 0.02467 | 42.5387 | 23729.6313 | 38.4902 | -18.1121 | 51.7896 | 38.4902 | -18.1121 | 30.714 | -90.7714 | -70.8491
665 | 0.055417 | 44.501 | 0.82239 | 5.1943e-05 | 0.025162 | 44.501 | 23362.2354 | 39.6507 | -20.2031 | 51.763 | 39.6507 | -20.203 | 30.6719 | -90.8313 | -70.9247
666 | 0.0555 | 46.4318 | 0.84756 | 0.0001008 | 0.025632 | 46.4317 | 22971.3967 | 40.6885 | -22.3687 | 51.7348 | 40.6884 | -22.3686 | 30.6296 | -90.8901 | -70.9964
667 | 0.055583 | 48.329 | 0.87319 | 0.00019415 | 0.026082 | 48.3288 | 22557.502 | 41.5988 | -24.6014 | 51.7051 | 41.5986 | -24.6014 | 30.5876 | -90.9479 | -71.0633
668 | 0.055667 | 50.1907 | 0.89927 | 0.00037098 | 0.026508 | 50.1904 | 22120.9606 | 42.3774 | -26.8935 | 51.6739 | 42.3771 | -26.8933 | 30.547 | -91.0045 | -71.1243
669 | 0.05575 | 52.0152 | 0.92578 | 0.00070295 | 0.026913 | 52.0145 | 21662.2045 | 43.0207 | -29.2369 | 51.6412 | 43.0202 | -29.2365 | 30.5089 | -91.06 | -71.178
670 | 0.055833 | 53.8005 | 0.95269 | 0.0013204 | 0.027293 | 53.7992 | 21181.6873 | 43.5255 | -31.6231 | 51.6071 | 43.5244 | -31.6224 | 30.4753 | -91.1141 | -71.2226
671 | 0.055917 | 55.5449 | 0.97998 | 0.002458 | 0.027649 | 55.5424 | 20679.8843 | 43.8891 | -34.0438 | 51.5717 | 43.8871 | -34.0423 | 30.4482 | -91.1671 | -71.2562
672 | 0.056 | 57.2466 | 1.0076 | 0.0045333 | 0.027977 | 57.242 | 20157.2917 | 44.1092 | -36.4903 | 51.5349 | 44.1057 | -36.4874 | 30.4304 | -91.2186 | -71.2769
673 | 0.056083 | 58.9039 | 1.0356 | 0.008281 | 0.028277 | 58.8956 | 19614.4263 | 44.1844 | -38.9538 | 51.4968 | 44.1782 | -38.9483 | 30.4245 | -91.2689 | -71.2833
674 | 0.056167 | 60.5151 | 1.0639 | 0.014978 | 0.028543 | 60.5001 | 19051.8247 | 44.1136 | -41.4254 | 51.4574 | 44.1027 | -41.4152 | 30.4331 | -91.3177 | -71.2746
675 | 0.05625 | 62.0786 | 1.0924 | 0.026818 | 0.028767 | 62.0518 | 18470.0431 | 43.8962 | -43.8962 | 51.4168 | 43.8773 | -43.8773 | 30.4586 | -91.365 | -71.251
676 | 0.056333 | 63.5929 | 1.1212 | 0.047508 | 0.028939 | 63.5454 | 17869.6568 | 43.5323 | -46.3572 | 51.3751 | 43.4998 | -46.3226 | 30.5029 | -91.4109 | -71.2132
677 | 0.056417 | 65.0564 | 1.1501 | 0.083223 | 0.029039 | 64.9732 | 17251.2592 | 43.0226 | -48.7995 | 51.3322 | 42.9675 | -48.7371 | 30.5674 | -91.4552 | -71.1628
678 | 0.0565 | 66.4676 | 1.1792 | 0.14404 | 0.029039 | 66.3236 | 16615.4615 | 42.3681 | -51.2142 | 51.2883 | 42.2763 | -51.1032 | 30.653 | -91.498 | -71.1021
679 | 0.056583 | 67.8252 | 1.2082 | 0.246 | 0.028897 | 67.5792 | 15962.8923 | 41.5705 | -53.5924 | 51.2433 | 41.4198 | -53.398 | 30.7603 | -91.5392 | -71.0337
680 | 0.056667 | 69.1277 | 1.2371 | 0.41377 | 0.028552 | 68.7139 | 15294.1965 | 40.6322 | -55.9255 | 51.1973 | 40.389 | -55.5907 | 30.8892 | -91.5788 | -70.9605
681 | 0.05675 | 70.3738 | 1.2657 | 0.68354 | 0.027929 | 69.6903 | 14610.0349 | 39.5559 | -58.2048 | 51.1504 | 39.1717 | -57.6395 | 31.0391 | -91.6167 | -70.8855
682 | 0.056833 | 71.5623 | 1.2936 | 1.1048 | 0.026949 | 70.4574 | 13911.0838 | 38.345 | -60.422 | 51.1026 | 37.753 | -59.4892 | 31.2088 | -91.6529 | -70.812
683 | 0.056917 | 72.6919 | 1.3205 | 1.739 | 0.025558 | 70.9529 | 13198.0339 | 37.0032 | -62.569 | 51.0539 | 36.118 | -61.0721 | 31.3965 | -91.6873 | -70.7429
684 | 0.057 | 73.7616 | 1.3461 | 2.6513 | 0.023756 | 71.1103 | 12471.5898 | 35.5349 | -64.6378 | 51.0044 | 34.2576 | -62.3144 | 31.5996 | -91.72 | -70.681
685 | 0.057083 | 74.7702 | 1.3699 | 3.8959 | 0.021631 | 70.8743 | 11732.4695 | 33.9449 | -66.6207 | 50.9542 | 32.1763 | -63.1495 | 31.8151 | -91.751 | -70.6286
686 | 0.057167 | 75.7166 | 1.3915 | 5.4992 | 0.01934 | 70.2175 | 10981.4034 | 32.2386 | -68.5105 | 50.9033 | 29.8971 | -63.5346 | 32.0395 | -91.7801 | -70.5876
687 | 0.05725 | 76.6001 | 1.4108 | 7.4504 | 0.017056 | 69.1497 | 10219.1335 | 30.4216 | -70.3001 | 50.8518 | 27.4626 | -63.4624 | 32.2696 | -91.8074 | -70.5592
688 | 0.057333 | 77.4195 | 1.4279 | 9.7049 | 0.014916 | 67.7146 | 9446.4131 | 28.5 | -71.9829 | 50.7997 | 24.9274 | -62.9595 | 32.502 | -91.8329 | -70.5437
689 | 0.057417 | 78.1742 | 1.4428 | 12.1978 | 0.012997 | 65.9764 | 8664.0058 | 26.4806 | -73.5526 | 50.747 | 22.3487 | -62.076 | 32.734 | -91.8564 | -70.5413
690 | 0.0575 | 78.8633 | 1.4558 | 14.8582 | 0.011325 | 64.0051 | 7872.6847 | 24.3701 | -75.0035 | 50.6939 | 19.7787 | -60.8724 | 32.9634 | -91.8781 | -70.5514
691 | 0.057583 | 79.4861 | 1.4671 | 17.62 | 0.0098883 | 61.8661 | 7073.2316 | 22.1759 | -76.33 | 50.6403 | 17.2601 | -59.4096 | 33.1884 | -91.8979 | -70.5735
692 | 0.057667 | 80.042 | 1.477 | 20.4262 | 0.0086617 | 59.6158 | 6266.4365 | 19.9056 | -77.5273 | 50.5864 | 14.8258 | -57.7428 | 33.4075 | -91.9158 | -70.6065
693 | 0.05775 | 80.5303 | 1.4857 | 23.2303 | 0.0076146 | 57.3001 | 5453.0964 | 17.5671 | -78.5909 | 50.5321 | 12.4996 | -55.9201 | 33.6197 | -91.9317 | -70.6496
694 | 0.057833 | 80.9507 | 1.4933 | 25.9956 | 0.0067178 | 54.9551 | 4634.0151 | 15.1686 | -79.5168 | 50.4775 | 10.2976 | -53.9817 | 33.8243 | -91.9457 | -70.7017
695 | 0.057917 | 81.3025 | 1.5 | 28.6936 | 0.0059459 | 52.6089 | 3810.0018 | 12.7185 | -80.3016 | 50.4228 | 8.2298 | -51.9612 | 34.0208 | -91.9577 | -70.7618
696 | 0.058 | 81.5855 | 1.5059 | 31.3028 | 0.005277 | 50.2827 | 2981.8707 | 10.2254 | -80.9422 | 50.3679 | 6.3021 | -49.8862 | 34.2087 | -91.9678 | -70.829
697 | 0.058083 | 81.7994 | 1.5112 | 33.8069 | 0.0046936 | 47.9925 | 2150.4398 | 7.698 | -81.4364 | 50.3128 | 4.5165 | -47.7795 | 34.3881 | -91.9759 | -70.9022
698 | 0.058167 | 81.9439 | 1.5159 | 36.1937 | 0.0041811 | 45.7502 | 1316.5308 | 5.1453 | -81.7822 | 50.2578 | 2.8727 | -45.6599 | 34.5587 | -91.982 | -70.9806
699 | 0.05825 | 82.0188 | 1.5201 | 38.4547 | 0.0037277 | 43.5641 | 480.9675 | 2.5763 | -81.9783 | 50.2027 | 1.3684 | -43.5426 | 34.7206 | -91.9862 | -71.0634
700 | 0.058333 | 82.024 | 1.5238 | 40.5836 | 0.003324 | 41.4404 | -355.4247 | 7.0315e-14 | -82.024 | 50.1477 | 3.5525e-14 | -41.4404 | 34.874 | -91.9884 | -71.1498
701 | 0.058417 | 81.9595 | 1.5272 | 42.5765 | 0.0029621 | 39.3831 | -1191.8192 | -2.5744 | -81.9191 | 50.0928 | -1.2371 | -39.3636 | 35.0189 | -91.9886 | -71.2391
702 | 0.0585 | 81.8254 | 1.5301 | 44.4308 | 0.0026358 | 37.3946 | -2027.3899 | -5.1379 | -81.6639 | 50.0381 | -2.348 | -37.3208 | 35.1555 | -91.9868 | -71.3307
703 | 0.058583 | 81.6217 | 1.5327 | 46.1454 | 0.0023396 | 35.4763 | -2861.3111 | -7.6813 | -81.2595 | 49.9835 | -3.3386 | -35.3188 | 35.2841 | -91.9831 | -71.424
704 | 0.058667 | 81.3486 | 1.5351 | 47.7201 | 0.0020693 | 33.6285 | -3692.759 | -10.1957 | -80.7071 | 49.9293 | -4.2148 | -33.3633 | 35.4049 | -91.9774 | -71.5183
705 | 0.05875 | 81.0063 | 1.5372 | 49.1555 | 0.0018212 | 31.8509 | -4520.9121 | -12.6722 | -80.009 | 49.8754 | -4.9826 | -31.4587 | 35.5183 | -91.9698 | -71.6134
706 | 0.058833 | 80.5952 | 1.539 | 50.4528 | 0.0015922 | 30.1425 | -5344.9522 | -15.102 | -79.1677 | 49.8218 | -5.6481 | -29.6085 | 35.6244 | -91.9602 | -71.7087
707 | 0.058917 | 80.1156 | 1.5406 | 51.6137 | 0.0013799 | 28.5019 | -6164.0652 | -17.4767 | -78.1862 | 49.7687 | -6.2175 | -27.8155 | 35.7235 | -91.9487 | -71.8038
708 | 0.059 | 79.568 | 1.542 | 52.6404 | 0.0011819 | 26.9277 | -6977.4417 | -19.7878 | -77.0683 | 49.7161 | -6.6966 | -26.0817 | 35.8161 | -91.9353 | -71.8984
709 | 0.059083 | 78.9529 | 1.5431 | 53.5352 | 0.00099645 | 25.4177 | -7784.2783 | -22.0272 | -75.818 | 49.664 | -7.0913 | -24.4084 | 35.9023 | -91.92 | -71.9922
710 | 0.059167 | 78.2709 | 1.5441 | 54.3009 | 0.00082187 | 23.9699 | -8583.7777 | -24.187 | -74.44 | 49.6124 | -7.4071 | -22.7968 | 35.9824 | -91.9029 | -72.0849
711 | 0.05925 | 77.5225 | 1.545 | 54.9403 | 0.00065677 | 22.5822 | -9375.15 | -26.2598 | -72.9394 | 49.5615 | -7.6494 | -21.2471 | 36.0568 | -91.8839 | -72.1762
712 | 0.059333 | 76.7086 | 1.5456 | 55.4565 | 0.00049991 | 21.2521 | -10157.6133 | -28.2383 | -71.3218 | 49.5113 | -7.8234 | -19.7597 | 36.1257 | -91.8631 | -72.2661
713 | 0.059417 | 75.8298 | 1.5461 | 55.8524 | 0.00035022 | 19.9774 | -10930.3946 | -30.1157 | -69.5932 | 49.4618 | -7.934 | -18.3344 | 36.1895 | -91.8404 | -72.3541
714 | 0.0595 | 74.8871 | 1.5465 | 56.1314 | 0.00020675 | 18.7557 | -11692.7302 | -31.8854 | -67.7599 | 49.4131 | -7.9858 | -16.9707 | 36.2483 | -91.816 | -72.4403
715 | 0.059583 | 73.8814 | 1.5467 | 56.2967 | 6.8622e-05 | 17.5846 | -12443.8671 | -33.5414 | -65.8288 | 49.3652 | -7.9833 | -15.668 | 36.3025 | -91.7899 | -72.5245
716 | 0.059667 | 72.8135 | 1.5467 | 56.3517 | -6.4913e-05 | 16.4618 | -13183.0629 | -35.0782 | -63.8069 | 49.3182 | -7.9305 | -14.4256 | 36.3523 | -91.762 | -72.6065
717 | 0.05975 | 71.6845 | 1.5467 | 56.2997 | -0.00019455 | 15.3848 | -13909.5874 | -36.4904 | -61.7019 | 49.2721 | -7.8315 | -13.2424 | 36.398 | -91.7325 | -72.6863
718 | 0.059833 | 70.4956 | 1.5465 | 56.1441 | -0.00032094 | 14.3515 | -14622.7226 | -37.7734 | -59.5214 | 49.2269 | -7.6899 | -12.1174 | 36.4398 | -91.7013 | -72.7637
719 | 0.059917 | 69.2478 | 1.5462 | 55.8883 | -0.00044465 | 13.3595 | -15321.7638 | -38.923 | -57.2735 | 49.1828 | -7.5091 | -11.0494 | 36.4779 | -91.6686 | -72.8388
720 | 0.06 | 67.9424 | 1.5457 | 55.5358 | -0.00056624 | 12.4066 | -16006.0204 | -39.9355 | -54.9665 | 49.1396 | -7.2924 | -10.0371 | 36.5126 | -91.6342 | -72.9114
721 | 0.060083 | 66.5806 | 1.5451 | 55.0899 | -0.0006862 | 11.4906 | -16674.8162 | -40.8077 | -52.609 | 49.0976 | -7.0427 | -9.0794 | 36.544 | -91.5983 | -72.9815
722 | 0.060167 | 65.1637 | 1.5445 | 54.5542 | -0.00080504 | 10.6095 | -17327.4903 | -41.5369 | -50.2095 | 49.0567 | -6.7627 | -8.1748 | 36.5725 | -91.561 | -73.0491
723 | 0.06025 | 63.6931 | 1.5437 | 53.932 | -0.00092322 | 9.7611 | -17963.3976 | -42.121 | -47.7769 | 49.0169 | -6.4551 | -7.3219 | 36.5981 | -91.5221 | -73.1141
724 | 0.060333 | 62.1703 | 1.5427 | 53.2268 | -0.0010412 | 8.9434 | -18581.9098 | -42.5585 | -45.3202 | 48.9783 | -6.1222 | -6.5195 | 36.6212 | -91.4819 | -73.1767
725 | 0.060417 | 60.5966 | 1.5417 | 52.4421 | -0.0011594 | 8.1545 | -19182.4155 | -42.8483 | -42.8483 | 48.9409 | -5.7661 | -5.7661 | 36.6417 | -91.4404 | -73.2366
726 | 0.0605 | 58.9737 | 1.5405 | 51.5813 | -0.0012783 | 7.3924 | -19764.3214 | -42.99 | -40.3703 | 48.9048 | -5.3888 | -5.0605 | 36.66 | -91.3975 | -73.2941
727 | 0.060583 | 57.3031 | 1.5392 | 50.6479 | -0.0013983 | 6.6553 | -20327.0522 | -42.9837 | -37.8952 | 48.8699 | -4.9922 | -4.4012 | 36.6762 | -91.3534 | -73.349
728 | 0.060667 | 55.5864 | 1.5379 | 49.6453 | -0.0015198 | 5.9412 | -20870.0518 | -42.8301 | -35.4321 | 48.8364 | -4.5777 | -3.787 | 36.6904 | -91.3081 | -73.4013
729 | 0.06075 | 53.8253 | 1.5363 | 48.577 | -0.0016434 | 5.2483 | -21392.7834 | -42.5304 | -32.9899 | 48.8043 | -4.147 | -3.2167 | 36.7028 | -91.2616 | -73.4512
730 | 0.060833 | 52.0215 | 1.5347 | 47.4466 | -0.0017695 | 4.575 | -21894.7302 | -42.0863 | -30.5775 | 48.7735 | -3.7012 | -2.6891 | 36.7136 | -91.214 | -73.4986
731 | 0.060917 | 50.1768 | 1.5329 | 46.2575 | -0.0018987 | 3.9194 | -22375.3962 | -41.5003 | -28.2035 | 48.7441 | -3.2416 | -2.203 | 36.7228 | -91.1654 | -73.5436
732 | 0.061 | 48.2929 | 1.531 | 45.0132 | -0.0020313 | 3.2797 | -22834.3059 | -40.7751 | -25.8766 | 48.7161 | -2.7691 | -1.7573 | 36.7306 | -91.1158 | -73.5861
733 | 0.061083 | 46.3717 | 1.529 | 43.7175 | -0.0021681 | 2.6542 | -23271.0058 | -39.9141 | -23.6051 | 48.6896 | -2.2846 | -1.3511 | 36.7371 | -91.0652 | -73.6263
734 | 0.061167 | 44.415 | 1.5268 | 42.3738 | -0.0023096 | 2.0412 | -23685.064 | -38.9212 | -21.3971 | 48.6645 | -1.7888 | -0.98338 | 36.7424 | -91.0138 | -73.664
735 | 0.06125 | 42.4248 | 1.5245 | 40.9858 | -0.0024565 | 1.439 | -24076.071 | -37.8008 | -19.2605 | 48.6409 | -1.2822 | -0.6533 | 36.7467 | -90.9616 | -73.6995
736 | 0.061333 | 40.403 | 1.5221 | 39.5572 | -0.0026094 | 0.84577 | -24443.6401 | -36.5577 | -17.2028 | 48.6189 | -0.76527 | -0.36011 | 36.75 | -90.9086 | -73.7326
737 | 0.061417 | 38.3516 | 1.5194 | 38.0918 | -0.0027692 | 0.25972 | -24787.4077 | -35.1973 | -15.2312 | 48.5983 | -0.23836 | -0.10315 | 36.7525 | -90.8549 | -73.7635
738 | 0.0615 | 36.2725 | 1.5167 | 36.5934 | -0.0029368 | -0.32094 | -25107.0337 | -33.7253 | -13.3528 | 48.5793 | 0.29841 | 0.11815 | 36.7543 | -90.8006 | -73.7921
739 | 0.061583 | 34.1677 | 1.5137 | 35.0658 | -0.003113 | -0.89811 | -25402.2018 | -32.1478 | -11.5739 | 48.5619 | 0.84501 | 0.30422 | 36.7553 | -90.7457 | -73.8185
740 | 0.061667 | 32.0394 | 1.5106 | 33.5131 | -0.003299 | -1.4737 | -25672.62 | -30.4713 | -9.9007 | 48.5459 | 1.4016 | 0.4554 | 36.7558 | -90.6903 | -73.8426
741 | 0.06175 | 29.8897 | 1.5073 | 31.9394 | -0.0034959 | -2.0497 | -25918.0205 | -28.7028 | -8.3389 | 48.5316 | 1.9684 | 0.57186 | 36.7558 | -90.6344 | -73.8646
742 | 0.061833 | 27.7205 | 1.5038 | 30.3488 | -0.003705 | -2.6283 | -26138.1602 | -26.8496 | -6.8938 | 48.5188 | 2.5458 | 0.65364 | 36.7554 | -90.5782 | -73.8845
743 | 0.061917 | 25.534 | 1.5001 | 28.7457 | -0.0039278 | -3.2117 | -26332.8212 | -24.9191 | -5.5701 | 48.5076 | 3.1344 | 0.70061 | 36.7547 | -90.5216 | -73.9021
744 | 0.062 | 23.3324 | 1.4962 | 27.1346 | -0.0041659 | -3.8022 | -26501.8104 | -22.9191 | -4.3721 | 48.498 | 3.7349 | 0.71247 | 36.7538 | -90.4648 | -73.9177
745 | 0.062083 | 21.1178 | 1.492 | 25.5202 | -0.0044212 | -4.4024 | -26644.9603 | -20.8578 | -3.3035 | 48.49 | 4.3482 | 0.68869 | 36.7528 | -90.4078 | -73.931
746 | 0.062167 | 18.8923 | 1.4876 | 23.9073 | -0.0046956 | -5.015 | -26762.1289 | -18.7433 | -2.3678 | 48.4836 | 4.9755 | 0.62855 | 36.7516 | -90.3506 | -73.9422
747 | 0.06225 | 16.6581 | 1.4829 | 22.301 | -0.0049915 | -5.6429 | -26853.1995 | -16.5842 | -1.5677 | 48.4787 | 5.6178 | 0.53104 | 36.7505 | -90.2934 | -73.9513
748 | 0.062333 | 14.4175 | 1.4779 | 20.7066 | -0.0053114 | -6.2892 | -26918.0816 | -14.389 | -0.90528 | 48.4755 | 6.2768 | 0.3949 | 36.7496 | -90.2361 | -73.9582
749 | 0.062417 | 12.1725 | 1.4726 | 19.1298 | -0.0056581 | -6.9573 | -26956.7103 | -12.1665 | -0.38235 | 48.4738 | 6.9539 | 0.21853 | 36.7488 | -90.1789 | -73.9629
750 | 0.0625 | 9.9254 | 1.467 | 17.5764 | -0.0060345 | -7.651 | -26969.0466 | -9.9254 | -2.6747e-14 | 48.4736 | 7.651 | 2.0618e-14 | 36.7484 | -90.1218 | -73.9653
751 | 0.062583 | 7.6784 | 1.4609 | 16.0526 | -0.006444 | -8.3742 | -26955.0776 | -7.6746 | 0.24118 | 48.4751 | 8.3701 | -0.26304 | 36.7483 | -90.0649 | -73.9655
752 | 0.062667 | 5.4336 | 1.4545 | 14.5649 | -0.00689 | -9.1313 | -26914.8162 | -5.4229 | 0.34118 | 48.4781 | 9.1132 | -0.57336 | 36.7488 | -90.0083 | -73.9634
753 | 0.06275 | 3.1933 | 1.4476 | 13.1202 | -0.007376 | -9.9268 | -26848.3015 | -3.1791 | 0.30052 | 48.4826 | 9.8828 | -0.9342 | 36.7499 | -89.9519 | -73.9589
754 | 0.062833 | 0.95964 | 1.4402 | 11.7255 | -0.0079053 | -10.7659 | -26755.5981 | -0.95208 | 0.12028 | 48.4886 | 10.681 | -1.3493 | 36.7519 | -89.8959 | -73.9519
755 | 0.062917 | -1.2652 | 1.4323 | 10.3882 | -0.0084812 | -11.6535 | -26636.7968 | 1.2496 | -0.19792 | 48.4962 | 11.51 | -1.823 | 36.7547 | -89.8403 | -73.9425
756 | 0.063 | -3.4791 | 1.4238 | 9.1159 | -0.009106 | -12.595 | -26492.014 | 3.4175 | -0.65192 | 48.5053 | 12.3719 | -2.3601 | 36.7586 | -89.7851 | -73.9305
757 | 0.063083 | -5.6798 | 1.4147 | 7.9158 | -0.009781 | -13.5957 | -26321.3919 | 5.543 | -1.239 | 48.5158 | 13.2683 | -2.9658 | 36.7637 | -89.7305 | -73.916
758 | 0.063167 | -7.8653 | 1.4049 | 6.7953 | -0.010506 | -14.6606 | -26125.0979 | 7.6182 | -1.956 | 48.5278 | 14.2 | -3.6459 | 36.7702 | -89.6765 | -73.8987
759 | 0.06325 | -10.0333 | 1.3944 | 5.761 | -0.011278 | -15.7943 | -25903.3251 | 9.6349 | -2.7992 | 48.5412 | 15.1671 | -4.4065 | 36.7783 | -89.6231 | -73.8788
760 | 0.063333 | -12.1818 | 1.3832 | 4.8184 | -0.012093 | -17.0002 | -25656.2915 | 11.5856 | -3.7644 | 48.5561 | 16.1682 | -5.2534 | 36.7881 | -89.5705 | -73.8562
761 | 0.063417 | -14.3087 | 1.3711 | 3.9719 | -0.01294 | -18.2806 | -25384.24 | 13.4627 | -4.8469 | 48.5723 | 17.1999 | -6.1923 | 36.7998 | -89.5185 | -73.831
762 | 0.0635 | -16.4118 | 1.3581 | 3.224 | -0.01381 | -19.6358 | -25087.4385 | 15.2593 | -6.0416 | 48.5899 | 18.2569 | -7.2284 | 36.8137 | -89.4674 | -73.8033
763 | 0.063583 | -18.4892 | 1.3443 | 2.5748 | -0.014687 | -21.064 | -24766.1789 | 16.9686 | -7.343 | 48.6089 | 19.3316 | -8.3655 | 36.8297 | -89.4171 | -73.7731
764 | 0.063667 | -20.5389 | 1.3296 | 2.022 | -0.015556 | -22.5609 | -24420.7776 | 18.5841 | -8.745 | 48.6292 | 20.4137 | -9.6059 | 36.8481 | -89.3677 | -73.7408
765 | 0.06375 | -22.5587 | 1.3141 | 1.5608 | -0.0164 | -24.1195 | -24051.5747 | 20.0999 | -10.2414 | 48.6507 | 21.4906 | -10.95 | 36.8688 | -89.3193 | -73.7065
766 | 0.063833 | -24.5468 | 1.2977 | 1.184 | -0.017204 | -25.7308 | -23658.9337 | 21.5105 | -11.8255 | 48.6735 | 22.5481 | -12.3959 | 36.8919 | -89.2718 | -73.6708
767 | 0.063917 | -26.5012 | 1.2805 | 0.88274 | -0.017959 | -27.384 | -23243.2413 | 22.8107 | -13.4902 | 48.6976 | 23.5705 | -13.9396 | 36.9174 | -89.2254 | -73.6338
768 | 0.064 | -28.42 | 1.2625 | 0.64697 | -0.018655 | -29.067 | -22804.9071 | 23.9958 | -15.2282 | 48.7228 | 24.5421 | -15.5749 | 36.9451 | -89.18 | -73.5962
769 | 0.064083 | -30.3014 | 1.2438 | 0.46628 | -0.01929 | -30.7677 | -22344.3627 | 25.0617 | -17.0319 | 48.7492 | 25.4474 | -17.294 | 36.9749 | -89.1358 | -73.5582
770 | 0.064167 | -32.1435 | 1.2246 | 0.33061 | -0.019864 | -32.4741 | -21862.062 | 26.0046 | -18.8935 | 48.7767 | 26.2721 | -19.0878 | 37.0067 | -89.0927 | -73.5204
771 | 0.06425 | -33.9445 | 1.2047 | 0.2307 | -0.020379 | -34.1752 | -21358.4801 | 26.8214 | -20.8048 | 48.8053 | 27.0037 | -20.9462 | 37.0402 | -89.0509 | -73.4832
772 | 0.064333 | -35.7027 | 1.1843 | 0.15851 | -0.020839 | -35.8612 | -20834.1133 | 27.5094 | -22.7577 | 48.8349 | 27.6315 | -22.8588 | 37.0753 | -89.0102 | -73.4468
773 | 0.064417 | -37.4163 | 1.1635 | 0.10726 | -0.021249 | -37.5235 | -20289.4782 | 28.0664 | -24.7438 | 48.8656 | 28.1468 | -24.8148 | 37.1117 | -88.9708 | -73.4116
774 | 0.0645 | -39.0837 | 1.1422 | 0.071502 | -0.021614 | -39.1552 | -19725.1117 | 28.4908 | -26.7546 | 48.8972 | 28.5429 | -26.8036 | 37.1493 | -88.9328 | -73.3778
775 | 0.064583 | -40.7033 | 1.1206 | 0.046967 | -0.021939 | -40.7502 | -19141.5698 | 28.7816 | -28.7816 | 48.9298 | 28.8148 | -28.8148 | 37.188 | -88.896 | -73.3456
776 | 0.064667 | -42.2734 | 1.0987 | 0.030401 | -0.022226 | -42.3038 | -18539.4277 | 28.9382 | -30.816 | 48.9633 | 28.959 | -30.8382 | 37.2275 | -88.8606 | -73.3152
777 | 0.06475 | -43.7927 | 1.0764 | 0.019392 | -0.022479 | -43.8121 | -17919.2789 | 28.9606 | -32.8494 | 48.9976 | 28.9734 | -32.8639 | 37.2678 | -88.8266 | -73.2867
778 | 0.064833 | -45.2595 | 1.054 | 0.01219 | -0.0227 | -45.2717 | -17281.7347 | 28.8495 | -34.873 | 49.0328 | 28.8573 | -34.8824 | 37.3087 | -88.794 | -73.2602
779 | 0.064917 | -46.6725 | 1.0313 | 0.0075502 | -0.022891 | -46.6801 | -16627.4234 | 28.6059 | -36.8785 | 49.0688 | 28.6105 | -36.8845 | 37.3502 | -88.7629 | -73.2357
780 | 0.065 | -48.0303 | 1.0084 | 0.0046077 | -0.023054 | -48.0349 | -15956.9901 | 28.2315 | -38.8573 | 49.1054 | 28.2342 | -38.8611 | 37.3922 | -88.7332 | -73.2133
781 | 0.065083 | -49.3316 | 0.98533 | 0.0027702 | -0.023188 | -49.3343 | -15271.0956 | 27.7285 | -40.8012 | 49.1428 | 27.73 | -40.8035 | 37.4345 | -88.7049 | -73.1929
782 | 0.065167 | -50.5751 | 0.96214 | 0.0016405 | -0.023296 | -50.5767 | -14570.4161 | 27.0995 | -42.7019 | 49.1809 | 27.1004 | -42.7033 | 37.4772 | -88.6782 | -73.1747
783 | 0.06525 | -51.7596 | 0.93884 | 0.00095672 | -0.023376 | -51.7605 | -13855.6424 | 26.3478 | -44.5516 | 49.2195 | 26.3483 | -44.5525 | 37.5202 | -88.653 | -73.1586
784 | 0.065333 | -52.884 | 0.91546 | 0.00054938 | -0.02343 | -52.8845 | -13127.479 | 25.477 | -46.3426 | 49.2587 | 25.4773 | -46.3431 | 37.5634 | -88.6293 | -73.1447
785 | 0.065417 | -53.9471 | 0.89203 | 0.00031057 | -0.023458 | -53.9475 | -12386.6438 | 24.4915 | -48.0673 | 49.2984 | 24.4916 | -48.0675 | 37.6067 | -88.6072 | -73.1328
786 | 0.0655 | -54.9481 | 0.86858 | 0.0001728 | -0.023459 | -54.9483 | -11633.8672 | 23.3958 | -49.7185 | 49.3386 | 23.3958 | -49.7187 | 37.6502 | -88.5866 | -73.1232
787 | 0.065583 | -55.8858 | 0.84512 | 9.4611e-05 | -0.023434 | -55.8859 | -10869.8914 | 22.1949 | -51.2895 | 49.3793 | 22.195 | -51.2895 | 37.6937 | -88.5675 | -73.1156
788 | 0.065667 | -56.7594 | 0.82168 | 5.0964e-05 | -0.023383 | -56.7595 | -10095.4696 | 20.8945 | -52.7736 | 49.4203 | 20.8946 | -52.7736 | 37.7373 | -88.55 | -73.1101
789 | 0.06575 | -57.5681 | 0.7983 | 2.7004e-05 | -0.023306 | -57.5681 | -9311.3653 | 19.5005 | -54.1647 | 49.4617 | 19.5005 | -54.1648 | 37.7809 | -88.5341 | -73.1068
790 | 0.065833 | -58.3111 | 0.775 | 1.4072e-05 | -0.023203 | -58.3111 | -8518.3516 | 18.0191 | -55.4571 | 49.5034 | 18.0191 | -55.4571 | 37.8243 | -88.5198 | -73.1055
791 | 0.065917 | -58.9876 | 0.75179 | 7.2097e-06 | -0.023074 | -58.9876 | -7717.2104 | 16.457 | -56.6454 | 49.5454 | 16.457 | -56.6454 | 37.8677 | -88.5071 | -73.1063
792 | 0.066 | -59.5971 | 0.72872 | 3.6314e-06 | -0.02292 | -59.5971 | -6908.7315 | 14.8212 | -57.7247 | 49.5875 | 14.8212 | -57.7247 | 37.9109 | -88.4959 | -73.1091
793 | 0.066083 | -60.1389 | 0.7058 | 1.7978e-06 | -0.02274 | -60.1389 | -6093.7122 | 13.1189 | -58.6906 | 49.6299 | 13.1189 | -58.6906 | 37.954 | -88.4863 | -73.114
794 | 0.066167 | -60.6125 | 0.68306 | 8.7463e-07 | -0.022535 | -60.6125 | -5272.9559 | 11.3577 | -59.5389 | 49.6724 | 11.3577 | -59.5389 | 37.9968 | -88.4783 | -73.1209
795 | 0.06625 | -61.0176 | 0.66052 | 4.1811e-07 | -0.022305 | -61.0176 | -4447.2721 | 9.5453 | -60.2664 | 49.7149 | 9.5453 | -60.2664 | 38.0393 | -88.4719 | -73.1298
796 | 0.066333 | -61.3536 | 0.63822 | 1.9637e-07 | -0.02205 | -61.3536 | -3617.4747 | 7.6896 | -60.8698 | 49.7575 | 7.6896 | -60.8698 | 38.0815 | -88.467 | -73.1406
797 | 0.066417 | -61.6204 | 0.61617 | 9.0599e-08 | -0.021771 | -61.6204 | -2784.3821 | 5.799 | -61.3469 | 49.8001 | 5.799 | -61.3469 | 38.1233 | -88.4637 | -73.1533
798 | 0.0665 | -61.8176 | 0.5944 | 4.106e-08 | -0.021467 | -61.8176 | -1948.8155 | 3.8816 | -61.6956 | 49.8427 | 3.8816 | -61.6956 | 38.1648 | -88.4619 | -73.168
799 | 0.066583 | -61.9452 | 0.57293 | 1.828e-08 | -0.02114 | -61.9452 | -1111.599 | 1.9457 | -61.9146 | 49.8852 | 1.9457 | -61.9146 | 38.2058 | -88.4617 | -73.1845
800 | 0.066667 | -62.0029 | 0.55179 | 7.9939e-09 | -0.020789 | -62.0029 | -273.5581 | 2.8102e-13 | -62.0029 | 49.9275 | 2.8102e-13 | -62.0029 | 38.2464 | -88.463 | -73.2029
801 | 0.06675 | -61.9908 | 0.531 | 3.4343e-09 | -0.020414 | -61.9908 | 564.481 | -1.9472 | -61.9602 | 49.9697 | -1.9472 | -61.9602 | 38.2864 | -88.4658 | -73.223
802 | 0.066833 | -61.9088 | 0.51059 | 1.4497e-09 | -0.020017 | -61.9088 | 1401.6919 | -3.8873 | -61.7867 | 50.0117 | -3.8873 | -61.7867 | 38.3259 | -88.4701 | -73.245
803 | 0.066917 | -61.7572 | 0.49057 | 6.014e-10 | -0.019597 | -61.7572 | 2237.249 | -5.8119 | -61.4831 | 50.0534 | -5.8119 | -61.4831 | 38.3649 | -88.4759 | -73.2686
804 | 0.067 | -61.536 | 0.47097 | 2.4528e-10 | -0.019155 | -61.536 | 3070.3286 | -7.7125 | -61.0508 | 50.0949 | -7.7125 | -61.0508 | 38.4032 | -88.4832 | -73.294
805 | 0.067083 | -61.2456 | 0.45182 | 9.8391e-11 | -0.018691 | -61.2456 | 3900.109 | -9.5809 | -60.4915 | 50.136 | -9.5809 | -60.4915 | 38.4409 | -88.4919 | -73.3211
806 | 0.067167 | -60.8861 | 0.43313 | 3.8841e-11 | -0.018206 | -60.8861 | 4725.7723 | -11.4089 | -59.8076 | 50.1767 | -11.4089 | -59.8076 | 38.4779 | -88.5021 | -73.3497
807 | 0.06725 | -60.4581 | 0.41492 | 1.5101e-11 | -0.017701 | -60.4581 | 5546.5041 | -13.1885 | -59.002 | 50.2171 | -13.1885 | -59.002 | 38.5142 | -88.5136 | -73.38
808 | 0.067333 | -59.9619 | 0.39722 | 5.787e-12 | -0.017175 | -59.9619 | 6361.4954 | -14.9119 | -58.078 | 50.257 | -14.9119 | -58.078 | 38.5498 | -88.5266 | -73.4117
809 | 0.067417 | -59.398 | 0.38005 | 2.1885e-12 | -0.01663 | -59.398 | 7169.9424 | -16.5715 | -57.0395 | 50.2964 | -16.5715 | -57.0395 | 38.5845 | -88.5409 | -73.445
810 | 0.0675 | -58.7671 | 0.36342 | 8.178e-13 | -0.016065 | -58.7671 | 7971.048 | -18.16 | -55.8908 | 50.3353 | -18.16 | -55.8908 | 38.6185 | -88.5566 | -73.4797
811 | 0.067583 | -58.0697 | 0.34735 | 3.0246e-13 | -0.015482 | -58.0697 | 8764.0223 | -19.6704 | -54.6367 | 50.3737 | -19.6704 | -54.6367 | 38.6517 | -88.5735 | -73.5159
812 | 0.067667 | -57.3066 | 0.33187 | 1.1092e-13 | -0.014881 | -57.3066 | 9548.0835 | -21.096 | -53.2824 | 50.4115 | -21.096 | -53.2824 | 38.684 | -88.5918 | -73.5534
813 | 0.06775 | -56.4786 | 0.31699 | 4.0429e-14 | -0.014263 | -56.4786 | 10322.4584 | -22.4304 | -51.8335 | 50.4487 | -22.4304 | -51.8335 | 38.7155 | -88.6113 | -73.5922
814 | 0.067833 | -55.5865 | 0.30272 | 1.4683e-14 | -0.013628 | -55.5865 | 11086.3835 | -23.6676 | -50.2962 | 50.4852 | -23.6676 | -50.2962 | 38.746 | -88.632 | -73.6323
815 | 0.067917 | -54.6312 | 0.2891 | 5.3301e-15 | -0.012976 | -54.6312 | 11839.1057 | -24.8021 | -48.6768 | 50.521 | -24.8021 | -48.6768 | 38.7757 | -88.654 | -73.6737
816 | 0.068 | -53.6137 | 0.27612 | 1.9407e-15 | -0.01231 | -53.6137 | 12579.8827 | -25.8286 | -46.982 | 50.5562 | -25.8286 | -46.982 | 38.8043 | -88.6771 | -73.7162
817 | 0.068083 | -52.5349 | 0.26381 | 7.1157e-16 | -0.011628 | -52.5349 | 13307.9843 | -26.7424 | -45.219 | 50.5906 | -26.7424 | -45.219 | 38.832 | -88.7014 | -73.7598
818 | 0.068167 | -51.396 | 0.25218 | 2.6395e-16 | -0.010933 | -51.396 | 14022.6924 | -27.5394 | -43.3951 | 50.6242 | -27.5394 | -43.3951 | 38.8588 | -88.7268 | -73.8045
819 | 0.06825 | -50.1982 | 0.24125 | 9.9555e-17 | -0.010224 | -50.1982 | 14723.3025 | -28.2156 | -41.518 | 50.657 | -28.2156 | -41.518 | 38.8845 | -88.7532 | -73.8503
820 | 0.068333 | -48.9426 | 0.23103 | 3.8401e-17 | -0.0095019 | -48.9426 | 15409.1238 | -28.7677 | -39.5954 | 50.689 | -28.7677 | -39.5954 | 38.9092 | -88.7807 | -73.8971
821 | 0.068417 | -47.6304 | 0.22153 | 1.5243e-17 | -0.0087681 | -47.6304 | 16079.4802 | -29.193 | -37.6354 | 50.7202 | -29.193 | -37.6354 | 38.9328 | -88.8092 | -73.9447
822 | 0.0685 | -46.2631 | 0.21276 | 6.2691e-18 | -0.0080231 | -46.2631 | 16733.7108 | -29.4892 | -35.6463 | 50.7505 | -29.4892 | -35.6463 | 38.9554 | -88.8387 | -73.9933
823 | 0.068583 | -44.842 | 0.20473 | 2.6911e-18 | -0.0072676 | -44.842 | 17371.1706 | -29.6545 | -33.6364 | 50.7799 | -29.6545 | -33.6364 | 38.9769 | -88.8692 | -74.0427
824 | 0.068667 | -43.3684 | 0.19747 | 1.2151e-18 | -0.0065023 | -43.3684 | 17991.2312 | -29.6877 | -31.6142 | 50.8084 | -29.6877 | -31.6142 | 38.9973 | -88.9005 | -74.0929
825 | 0.06875 | -41.8439 | 0.19096 | 5.8169e-19 | -0.0057279 | -41.8439 | 18593.2814 | -29.5881 | -29.5881 | 50.8359 | -29.5881 | -29.5881 | 39.0166 | -88.9328 | -74.1438
826 | 0.068833 | -40.27 | 0.18524 | 2.9766e-19 | -0.0049454 | -40.27 | 19176.7276 | -29.3556 | -27.5667 | 50.8624 | -29.3556 | -27.5667 | 39.0348 | -88.9658 | -74.1954
827 | 0.068917 | -38.6483 | 0.18029 | 1.6412e-19 | -0.0041553 | -38.6483 | 19740.9947 | -28.9905 | -25.5586 | 50.888 | -28.9905 | -25.5586 | 39.0519 | -88.9997 | -74.2477
828 | 0.069 | -36.9804 | 0.17614 | 9.8262e-20 | -0.0033586 | -36.9804 | 20285.5265 | -28.4939 | -23.5722 | 50.9126 | -28.4939 | -23.5722 | 39.0678 | -89.0343 | -74.3005
829 | 0.069083 | -35.268 | 0.17278 | 6.4333e-20 | -0.002556 | -35.268 | 20809.7864 | -27.8672 | -21.616 | 50.9361 | -27.8672 | -21.616 | 39.0826 | -89.0697 | -74.3538
830 | 0.069167 | -33.5127 | 0.17022 | 4.6348e-20 | -0.0017484 | -33.5127 | 21313.2575 | -27.1123 | -19.6983 | 50.9587 | -27.1123 | -19.6983 | 39.0962 | -89.1057 | -74.4076
831 | 0.06925 | -31.7163 | 0.16847 | 3.6931e-20 | -0.00093641 | -31.7163 | 21795.4438 | -26.232 | -17.8272 | 50.9801 | -26.232 | -17.8272 | 39.1087 | -89.1424 | -74.4619
832 | 0.069333 | -29.8807 | 0.16754 | 3.2669e-20 | -0.00012099 | -29.8807 | 22255.8699 | -25.2291 | -16.0109 | 51.0005 | -25.2291 | -16.0109 | 39.12 | -89.1797 | -74.5165
833 | 0.069417 | -28.0077 | 0.16741 | 3.2154e-20 | 0.0006971 | -28.0077 | 22694.0821 | -24.1074 | -14.2571 | 51.0198 | -24.1074 | -14.2571 | 39.1302 | -89.2176 | -74.5714
834 | 0.0695 | -26.099 | 0.16811 | 3.5232e-20 | 0.001517 | -26.099 | 23109.6487 | -22.8707 | -12.5733 | 51.038 | -22.8707 | -12.5733 | 39.1392 | -89.256 | -74.6266
835 | 0.069583 | -24.1567 | 0.16963 | 4.293e-20 | 0.002338 | -24.1567 | 23502.1602 | -21.5238 | -10.9669 | 51.0552 | -21.5238 | -10.9669 | 39.147 | -89.2949 | -74.682
836 | 0.069667 | -22.1826 | 0.17197 | 5.8017e-20 | 0.0031592 | -22.1826 | 23871.2298 | -20.0714 | -9.4449 | 51.0712 | -20.0714 | -9.4449 | 39.1536 | -89.3343 | -74.7376
837 | 0.06975 | -20.1788 | 0.17513 | 8.6594e-20 | 0.0039798 | -20.1788 | 24216.494 | -18.5192 | -8.014 | 51.086 | -18.5192 | -8.014 | 39.1591 | -89.3741 | -74.7933
838 | 0.069833 | -18.1472 | 0.17911 | 1.4197e-19 | 0.0047989 | -18.1472 | 24537.6127 | -16.8729 | -6.6804 | 51.0998 | -16.8729 | -6.6804 | 39.1634 | -89.4142 | -74.8491
839 | 0.069917 | -16.0899 | 0.1839 | 2.5399e-19 | 0.0056159 | -16.0899 | 24834.2696 | -15.1387 | -5.4503 | 51.1124 | -15.1387 | -5.4503 | 39.1665 | -89.4547 | -74.9049
840 | 0.07 | -14.0089 | 0.18952 | 4.9228e-19 | 0.0064297 | -14.0089 | 25106.1727 | -13.3232 | -4.329 | 51.1238 | -13.3232 | -4.329 | 39.1684 | -89.4955 | -74.9606
841 | 0.070083 | -11.9062 | 0.19595 | 1.0256e-18 | 0.0072398 | -11.9062 | 25353.0542 | -11.4335 | -3.3217 | 51.1341 | -11.4335 | -3.3217 | 39.1692 | -89.5366 | -75.0163
842 | 0.070167 | -9.7841 | 0.20319 | 2.2784e-18 | 0.0080451 | -9.7841 | 25574.6711 | -9.4767 | -2.4332 | 51.1433 | -9.4767 | -2.4332 | 39.1689 | -89.5778 | -75.0718
843 | 0.07025 | -7.6445 | 0.21124 | 5.3534e-18 | 0.008845 | -7.6445 | 25770.8053 | -7.4604 | -1.6676 | 51.1513 | -7.4604 | -1.6676 | 39.1673 | -89.6193 | -75.1271
844 | 0.070333 | -5.4896 | 0.22008 | 1.3199e-17 | 0.0096387 | -5.4896 | 25941.264 | -5.3924 | -1.0287 | 51.1581 | -5.3924 | -1.0287 | 39.1647 | -89.6609 | -75.1822
845 | 0.070417 | -3.3217 | 0.22972 | 3.3892e-17 | 0.010425 | -3.3217 | 26085.8795 | -3.2808 | -0.51962 | 51.1638 | -3.2808 | -0.51962 | 39.1609 | -89.7026 | -75.237
846 | 0.0705 | -1.1427 | 0.24014 | 8.9982e-17 | 0.011204 | -1.1427 | 26204.5098 | -1.1337 | -0.14322 | 51.1683 | -1.1337 | -0.14322 | 39.156 | -89.7443 | -75.2915
847 | 0.070583 | 1.045 | 0.25135 | 2.4538e-16 | 0.011974 | 1.045 | 26297.0383 | 1.0404 | 0.098347 | 51.1717 | 1.0404 | 0.098347 | 39.1499 | -89.7861 | -75.3456
848 | 0.070667 | 3.2394 | 0.26332 | 6.8313e-16 | 0.012735 | 3.2394 | 26363.3745 | 3.233 | 0.2034 | 51.1739 | 3.233 | 0.2034 | 39.1428 | -89.8279 | -75.3993
849 | 0.07075 | 5.4382 | 0.27606 | 1.9309e-15 | 0.013486 | 5.4382 | 26403.4535 | 5.4355 | 0.17082 | 51.175 | 5.4355 | 0.17082 | 39.1345 | -89.8696 | -75.4525
850 | 0.070833 | 7.6392 | 0.28954 | 5.5139e-15 | 0.014225 | 7.6392 | 26417.2364 | 7.6392 | 2.1522e-14 | 51.1749 | 7.6392 | 2.1522e-14 | 39.1252 | -89.9112 | -75.5052
851 | 0.070917 | 9.8403 | 0.30377 | 1.5838e-14 | 0.014954 | 9.8403 | 26404.7101 | 9.8355 | -0.30909 | 51.1737 | 9.8355 | -0.30909 | 39.1148 | -89.9527 | -75.5573
852 | 0.071 | 12.0393 | 0.31872 | 4.5586e-14 | 0.015669 | 12.0393 | 26365.8878 | 12.0155 | -0.75595 | 51.1714 | 12.0155 | -0.75595 | 39.1034 | -89.994 | -75.6088
853 | 0.071083 | 14.2339 | 0.33439 | 1.3103e-13 | 0.016372 | 14.2339 | 26300.8082 | 14.1708 | -1.3395 | 51.1679 | 14.1708 | -1.3395 | 39.0909 | -90.0351 | -75.6597
854 | 0.071167 | 16.422 | 0.35076 | 3.7505e-13 | 0.017061 | 16.422 | 26209.5363 | 16.2926 | -2.0582 | 51.1634 | 16.2926 | -2.0582 | 39.0774 | -90.076 | -75.7098
855 | 0.07125 | 18.6015 | 0.36782 | 1.0663e-12 | 0.017736 | 18.6015 | 26092.1627 | 18.3724 | -2.9099 | 51.1577 | 18.3724 | -2.9099 | 39.0629 | -90.1165 | -75.7593
856 | 0.071333 | 20.77 | 0.38556 | 3.0047e-12 | 0.018395 | 20.77 | 25948.8039 | 20.4021 | -3.8919 | 51.1509 | 20.4021 | -3.8919 | 39.0475 | -90.1568 | -75.8079
857 | 0.071417 | 22.9255 | 0.40396 | 8.3774e-12 | 0.019039 | 22.9255 | 25779.602 | 22.3734 | -5.0011 | 51.1431 | 22.3734 | -5.0011 | 39.031 | -90.1967 | -75.8557
858 | 0.0715 | 25.0659 | 0.42299 | 2.3075e-11 | 0.019666 | 25.0659 | 25584.7246 | 24.2784 | -6.2336 | 51.1341 | 24.2784 | -6.2336 | 39.0136 | -90.2363 | -75.9027
859 | 0.071583 | 27.189 | 0.44266 | 6.2709e-11 | 0.020276 | 27.189 | 25364.3647 | 26.1094 | -7.5855 | 51.1242 | 26.1094 | -7.5855 | 38.9953 | -90.2754 | -75.9488
860 | 0.071667 | 29.2926 | 0.46294 | 1.6798e-10 | 0.020869 | 29.2926 | 25118.7402 | 27.8589 | -9.0519 | 51.1132 | 27.8589 | -9.0519 | 38.9761 | -90.3141 | -75.9939
861 | 0.07175 | 31.3747 | 0.48381 | 4.4314e-10 | 0.021444 | 31.3747 | 24848.0942 | 29.5199 | -10.6278 | 51.1011 | 29.5199 | -10.6278 | 38.9561 | -90.3522 | -76.038
862 | 0.071833 | 33.4333 | 0.50525 | 1.1505e-09 | 0.021999 | 33.4333 | 24552.6944 | 31.0855 | -12.3076 | 51.0881 | 31.0855 | -12.3076 | 38.9351 | -90.3899 | -76.0811
863 | 0.071917 | 35.4662 | 0.52725 | 2.9384e-09 | 0.022535 | 35.4662 | 24232.833 | 32.5492 | -14.0853 | 51.074 | 32.5492 | -14.0853 | 38.9134 | -90.427 | -76.1232
864 | 0.072 | 37.4714 | 0.54978 | 7.379e-09 | 0.023052 | 37.4714 | 23888.8262 | 33.9051 | -15.9545 | 51.059 | 33.9051 | -15.9545 | 38.8908 | -90.4635 | -76.1642
865 | 0.072083 | 39.447 | 0.57284 | 1.8215e-08 | 0.023548 | 39.447 | 23521.0141 | 35.1475 | -17.9085 | 51.0431 | 35.1475 | -17.9085 | 38.8674 | -90.4994 | -76.204
866 | 0.072167 | 41.3909 | 0.59638 | 4.4191e-08 | 0.024023 | 41.3909 | 23129.7603 | 36.2711 | -19.9402 | 51.0262 | 36.2711 | -19.9402 | 38.8433 | -90.5346 | -76.2427
867 | 0.07225 | 43.3013 | 0.62041 | 1.0535e-07 | 0.024476 | 43.3013 | 22715.4515 | 37.2712 | -22.0421 | 51.0084 | 37.2712 | -22.0421 | 38.8185 | -90.5692 | -76.2802
868 | 0.072333 | 45.1762 | 0.64488 | 2.4679e-07 | 0.024908 | 45.1762 | 22278.4971 | 38.1435 | -24.2066 | 50.9897 | 38.1435 | -24.2066 | 38.7929 | -90.603 | -76.3165
869 | 0.072417 | 47.0138 | 0.66979 | 5.6809e-07 | 0.025318 | 47.0138 | 21819.3291 | 38.8842 | -26.4256 | 50.9701 | 38.8842 | -26.4256 | 38.7667 | -90.6361 | -76.3516
870 | 0.0725 | 48.8121 | 0.69511 | 1.285e-06 | 0.025704 | 48.8121 | 21338.4011 | 39.4899 | -28.6911 | 50.9497 | 39.4898 | -28.6911 | 38.7398 | -90.6685 | -76.3854
871 | 0.072583 | 50.5696 | 0.72081 | 2.8566e-06 | 0.026068 | 50.5696 | 20836.1884 | 39.9578 | -30.9944 | 50.9285 | 39.9578 | -30.9944 | 38.7123 | -90.7 | -76.4178
872 | 0.072667 | 52.2843 | 0.74688 | 6.2415e-06 | 0.026408 | 52.2843 | 20313.1872 | 40.2857 | -33.3272 | 50.9065 | 40.2857 | -33.3272 | 38.6843 | -90.7308 | -76.4489
873 | 0.07275 | 53.9545 | 0.77329 | 1.3405e-05 | 0.026725 | 53.9545 | 19769.9141 | 40.4719 | -35.6808 | 50.8837 | 40.4719 | -35.6808 | 38.6557 | -90.7607 | -76.4787
874 | 0.072833 | 55.5787 | 0.80001 | 2.8308e-05 | 0.027017 | 55.5787 | 19206.9059 | 40.5151 | -38.0462 | 50.8601 | 40.5151 | -38.0462 | 38.6266 | -90.7897 | -76.507
875 | 0.072917 | 57.1551 | 0.82703 | 5.8782e-05 | 0.027285 | 57.1551 | 18624.7189 | 40.4148 | -40.4148 | 50.8359 | 40.4147 | -40.4147 | 38.5971 | -90.8178 | -76.5339
876 | 0.073 | 58.6823 | 0.85432 | 0.00012005 | 0.027529 | 58.6822 | 18023.9282 | 40.1708 | -42.7776 | 50.8109 | 40.1707 | -42.7775 | 38.5672 | -90.845 | -76.5592
877 | 0.073083 | 60.1586 | 0.88185 | 0.00024121 | 0.027747 | 60.1584 | 17405.1272 | 39.7836 | -45.1257 | 50.7853 | 39.7835 | -45.1255 | 38.5371 | -90.8713 | -76.5829
878 | 0.073167 | 61.5827 | 0.90959 | 0.00047686 | 0.027939 | 61.5822 | 16768.9273 | 39.2543 | -47.4503 | 50.759 | 39.254 | -47.4499 | 38.5071 | -90.8966 | -76.6049
879 | 0.07325 | 62.953 | 0.93753 | 0.00092779 | 0.028106 | 62.9521 | 16115.9568 | 38.5843 | -49.7426 | 50.7321 | 38.5838 | -49.7419 | 38.4773 | -90.9209 | -76.6251
880 | 0.073333 | 64.2682 | 0.96564 | 0.0017769 | 0.028245 | 64.2664 | 15446.8608 | 37.7759 | -51.9941 | 50.7046 | 37.7749 | -51.9926 | 38.4482 | -90.9442 | -76.6431
881 | 0.073417 | 65.527 | 0.99388 | 0.0033506 | 0.028356 | 65.5237 | 14762.3 | 36.8317 | -54.1961 | 50.6766 | 36.8298 | -54.1934 | 38.4207 | -90.9666 | -76.6587
882 | 0.0735 | 66.7282 | 1.0222 | 0.0062217 | 0.028438 | 66.722 | 14062.9508 | 35.7548 | -56.3405 | 50.6481 | 35.7514 | -56.3352 | 38.3957 | -90.9878 | -76.6716
883 | 0.073583 | 67.8705 | 1.0507 | 0.011378 | 0.028485 | 67.8591 | 13349.5039 | 34.5489 | -58.419 | 50.619 | 34.5431 | -58.4092 | 38.3749 | -91.008 | -76.6813
884 | 0.073667 | 68.9527 | 1.0792 | 0.020496 | 0.028495 | 68.9322 | 12622.6638 | 33.2182 | -60.4237 | 50.5895 | 33.2084 | -60.4058 | 38.36 | -91.0272 | -76.6874
885 | 0.07375 | 69.9739 | 1.1077 | 0.036364 | 0.028457 | 69.9375 | 11883.1485 | 31.7675 | -62.3472 | 50.5596 | 31.751 | -62.3148 | 38.3536 | -91.0452 | -76.6898
886 | 0.073833 | 70.9329 | 1.1361 | 0.063539 | 0.028359 | 70.8694 | 11131.6884 | 30.2018 | -64.182 | 50.5293 | 30.1747 | -64.1245 | 38.3581 | -91.0622 | -76.6884
887 | 0.073917 | 71.8289 | 1.1645 | 0.1093 | 0.028182 | 71.7196 | 10369.0255 | 28.5267 | -65.9213 | 50.4986 | 28.4833 | -65.821 | 38.376 | -91.0781 | -76.6836
888 | 0.074 | 72.6608 | 1.1927 | 0.18496 | 0.027896 | 72.4758 | 9595.9133 | 26.7482 | -67.5583 | 50.4675 | 26.6801 | -67.3863 | 38.4093 | -91.0928 | -76.6764
889 | 0.074083 | 73.4279 | 1.2206 | 0.3076 | 0.027462 | 73.1203 | 8813.1151 | 24.8728 | -69.0869 | 50.4362 | 24.7686 | -68.7975 | 38.4595 | -91.1064 | -76.6679
890 | 0.074167 | 74.1294 | 1.248 | 0.50185 | 0.02683 | 73.6276 | 8021.4041 | 22.9072 | -70.5013 | 50.4045 | 22.7522 | -70.024 | 38.5273 | -91.1188 | -76.6597
891 | 0.07425 | 74.7646 | 1.2748 | 0.80131 | 0.025944 | 73.9633 | 7221.5622 | 20.8587 | -71.796 | 50.3727 | 20.6351 | -71.0265 | 38.6127 | -91.1301 | -76.6533
892 | 0.074333 | 75.3328 | 1.3008 | 1.2482 | 0.024758 | 74.0846 | 6414.3792 | 18.7345 | -72.9661 | 50.3406 | 18.4241 | -71.7571 | 38.715 | -91.1403 | -76.6505
893 | 0.074417 | 75.8335 | 1.3255 | 1.8899 | 0.023254 | 73.9436 | 5600.6524 | 16.5426 | -74.0072 | 50.3083 | 16.1303 | -72.1628 | 38.8327 | -91.1493 | -76.6528
894 | 0.0745 | 76.2661 | 1.3488 | 2.7707 | 0.021466 | 73.4954 | 4781.1853 | 14.2908 | -74.9152 | 50.2759 | 13.7717 | -72.1936 | 38.9637 | -91.1571 | -76.6614
895 | 0.074583 | 76.6302 | 1.3703 | 3.9215 | 0.019479 | 72.7087 | 3956.7872 | 11.9876 | -75.6868 | 50.2434 | 11.3741 | -71.8135 | 39.1054 | -91.1637 | -76.6771
896 | 0.074667 | 76.9254 | 1.3897 | 5.3496 | 0.017417 | 71.5759 | 3128.2723 | 9.6413 | -76.3189 | 50.2108 | 8.9708 | -71.0115 | 39.2551 | -91.1692 | -76.7006
897 | 0.07475 | 77.1515 | 1.4072 | 7.0358 | 0.0154 | 70.1157 | 2296.4587 | 7.2606 | -76.8091 | 50.1781 | 6.5985 | -69.8045 | 39.4101 | -91.1735 | -76.7318
898 | 0.074833 | 77.3081 | 1.4226 | 8.9395 | 0.01352 | 68.3686 | 1462.1678 | 4.8542 | -77.1556 | 50.1455 | 4.2929 | -68.2337 | 39.5677 | -91.1766 | -76.7707
899 | 0.074917 | 77.3951 | 1.4361 | 11.0075 | 0.011826 | 66.3876 | 626.2237 | 2.431 | -77.3569 | 50.1128 | 2.0853 | -66.3549 | 39.7259 | -91.1785 | -76.8168
900 | 0.075 | 77.4125 | 1.4479 | 13.184 | 0.010334 | 64.2284 | -210.5482 | 3.6035e-13 | -77.4125 | 50.0802 | 2.9898e-13 | -64.2284 | 39.8829 | -91.1793 | -76.8696
901 | 0.075083 | 77.36 | 1.4582 | 15.4169 | 0.0090355 | 61.9431 | -1047.3215 | -2.4299 | -77.3219 | 50.0477 | -1.9457 | -61.9125 | 40.037 | -91.1789 | -76.9285
902 | 0.075167 | 77.2379 | 1.4673 | 17.6611 | 0.0079117 | 59.5769 | -1883.27 | -4.8498 | -77.0855 | 50.0153 | -3.7409 | -59.4593 | 40.1873 | -91.1773 | -76.9926
903 | 0.07525 | 77.0462 | 1.4752 | 19.8791 | 0.0069396 | 57.1671 | -2717.568 | -7.2507 | -76.7043 | 49.983 | -5.3799 | -56.9134 | 40.3329 | -91.1746 | -77.0614
904 | 0.075333 | 76.7851 | 1.4821 | 22.0414 | 0.0060967 | 54.7437 | -3549.3917 | -9.6237 | -76.1796 | 49.9509 | -6.8612 | -54.312 | 40.4731 | -91.1707 | -77.1342
905 | 0.075417 | 76.4547 | 1.4882 | 24.1246 | 0.0053624 | 52.3301 | -4377.9197 | -11.9602 | -75.5135 | 49.919 | -8.1862 | -51.6859 | 40.6075 | -91.1657 | -77.2103
906 | 0.0755 | 76.0555 | 1.4936 | 26.1111 | 0.0047192 | 49.9444 | -5202.3336 | -14.2514 | -74.7084 | 49.8874 | -9.3587 | -49.0598 | 40.7359 | -91.1595 | -77.2891
907 | 0.075583 | 75.5878 | 1.4983 | 27.9876 | 0.0041522 | 47.6002 | -6021.8195 | -16.489 | -73.7674 | 49.856 | -10.3837 | -46.4538 | 40.858 | -91.1522 | -77.3701
908 | 0.075667 | 75.0521 | 1.5025 | 29.7445 | 0.003649 | 45.3075 | -6835.568 | -18.6647 | -72.6942 | 49.8249 | -11.2675 | -43.8841 | 40.9738 | -91.1438 | -77.4527
909 | 0.07575 | 74.4487 | 1.5061 | 31.375 | 0.0031996 | 43.0737 | -7642.7755 | -20.7705 | -71.4927 | 49.7942 | -12.0172 | -41.3634 | 41.0833 | -91.1343 | -77.5364
910 | 0.075833 | 73.7785 | 1.5093 | 32.8746 | 0.0027955 | 40.9039 | -8442.6448 | -22.7988 | -70.1675 | 49.7638 | -12.64 | -38.9019 | 41.1865 | -91.1237 | -77.6208
911 | 0.075917 | 73.0419 | 1.5121 | 34.2405 | 0.0024297 | 38.8013 | -9234.3861 | -24.742 | -68.7237 | 49.7338 | -13.1435 | -36.5074 | 41.2837 | -91.112 | -77.7056
912 | 0.076 | 72.2396 | 1.5145 | 35.4716 | 0.0020965 | 36.768 | -10017.2175 | -26.5932 | -67.1667 | 49.7042 | -13.5352 | -34.186 | 41.3748 | -91.0992 | -77.7903
913 | 0.076083 | 71.3726 | 1.5166 | 36.5677 | 0.001791 | 34.8049 | -10790.3658 | -28.3455 | -65.5025 | 49.675 | -13.8227 | -31.9423 | 41.4601 | -91.0854 | -77.8747
914 | 0.076167 | 70.4415 | 1.5184 | 37.5296 | 0.0015093 | 32.9119 | -11553.0676 | -29.9925 | -63.7374 | 49.6463 | -14.0132 | -29.7796 | 41.5397 | -91.0706 | -77.9584
915 | 0.07625 | 69.4474 | 1.5199 | 38.3589 | 0.0012477 | 31.0885 | -12304.5696 | -31.5285 | -61.8781 | 49.6181 | -14.1139 | -27.7 | 41.6139 | -91.0548 | -78.0412
916 | 0.076333 | 68.3911 | 1.5212 | 39.0577 | 0.0010036 | 29.3334 | -13044.1297 | -32.9477 | -59.9316 | 49.5904 | -14.1315 | -25.7051 | 41.6829 | -91.038 | -78.1229
917 | 0.076417 | 67.2737 | 1.5222 | 39.6285 | 0.00077427 | 27.6452 | -13771.0174 | -34.2451 | -57.9053 | 49.5633 | -14.0725 | -23.7954 | 41.7469 | -91.0202 | -78.2033
918 | 0.0765 | 66.0963 | 1.523 | 40.0744 | 0.00055768 | 26.0219 | -14484.5149 | -35.4162 | -55.807 | 49.5368 | -13.9432 | -21.971 | 41.8061 | -91.0015 | -78.2821
919 | 0.076583 | 64.86 | 1.5235 | 40.3985 | 0.00035193 | 24.4615 | -15183.9175 | -36.4567 | -53.6445 | 49.5108 | -13.7494 | -20.2317 | 41.8607 | -90.9818 | -78.3593
920 | 0.076667 | 63.5661 | 1.5239 | 40.6043 | 0.00015536 | 22.9618 | -15868.5345 | -37.3632 | -51.426 | 49.4855 | -13.4966 | -18.5765 | 41.9111 | -90.9612 | -78.4347
921 | 0.07675 | 62.2157 | 1.524 | 40.6954 | -3.3486e-05 | 21.5203 | -16537.6897 | -38.1324 | -49.16 | 49.4608 | -13.1899 | -17.0043 | 41.9573 | -90.9398 | -78.5082
922 | 0.076833 | 60.8102 | 1.524 | 40.6758 | -0.00021591 | 20.1345 | -17190.7223 | -38.7619 | -46.8551 | 49.4367 | -12.8342 | -15.5139 | 41.9996 | -90.9175 | -78.5797
923 | 0.076917 | 59.351 | 1.5238 | 40.5492 | -0.00039309 | 18.8019 | -17826.9872 | -39.2496 | -44.5199 | 49.4134 | -12.4339 | -14.1035 | 42.0383 | -90.8944 | -78.6491
924 | 0.077 | 57.8396 | 1.5234 | 40.3197 | -0.00056612 | 17.5199 | -18445.8561 | -39.5939 | -42.1632 | 49.3907 | -11.9932 | -12.7714 | 42.0735 | -90.8705 | -78.7164
925 | 0.077083 | 56.2772 | 1.5228 | 39.9913 | -0.00073599 | 16.2859 | -19046.7176 | -39.794 | -39.794 | 49.3688 | -11.5159 | -11.5159 | 42.1054 | -90.8458 | -78.7815
926 | 0.077167 | 54.6656 | 1.5221 | 39.5683 | -0.00090366 | 15.0974 | -19628.9782 | -39.8495 | -37.4212 | 49.3476 | -11.0055 | -10.3349 | 42.1343 | -90.8204 | -78.8443
927 | 0.07725 | 53.0063 | 1.5212 | 39.0546 | -0.00107 | 13.9516 | -20192.0629 | -39.7606 | -35.0537 | 49.3272 | -10.4653 | -9.2264 | 42.1603 | -90.7942 | -78.9049
928 | 0.077333 | 51.3008 | 1.5201 | 38.4547 | -0.0012359 | 12.8461 | -20735.4154 | -39.528 | -32.7004 | 49.3076 | -9.8981 | -8.1884 | 42.1836 | -90.7674 | -78.9632
929 | 0.077417 | 49.5509 | 1.5189 | 37.7727 | -0.0014022 | 11.7782 | -21258.499 | -39.1529 | -30.3701 | 49.2888 | -9.3066 | -7.219 | 42.2045 | -90.74 | -79.0191
930 | 0.0775 | 47.7583 | 1.5175 | 37.0129 | -0.0015698 | 10.7454 | -21760.797 | -38.6373 | -28.0716 | 49.2707 | -8.6932 | -6.316 | 42.2229 | -90.7119 | -79.0728
931 | 0.077583 | 45.9247 | 1.5159 | 36.1797 | -0.0017394 | 9.7451 | -22241.8131 | -37.9834 | -25.8135 | 49.2535 | -8.06 | -5.4775 | 42.2392 | -90.6832 | -79.1241
932 | 0.077667 | 44.052 | 1.5142 | 35.2773 | -0.001912 | 8.7747 | -22701.0721 | -37.1943 | -23.6042 | 49.2372 | -7.4087 | -4.7017 | 42.2535 | -90.6539 | -79.1731
933 | 0.07775 | 42.1418 | 1.5122 | 34.3101 | -0.0020884 | 7.8317 | -23138.1203 | -36.2732 | -21.4519 | 49.2217 | -6.7411 | -3.9867 | 42.2659 | -90.6242 | -79.2198
934 | 0.077833 | 40.1962 | 1.5102 | 33.2827 | -0.0022697 | 6.9136 | -23552.526 | -35.2242 | -19.3647 | 49.207 | -6.0584 | -3.3306 | 42.2766 | -90.5939 | -79.2642
935 | 0.077917 | 38.217 | 1.5079 | 32.1994 | -0.0024567 | 6.0177 | -23943.8795 | -34.0516 | -17.3502 | 49.1932 | -5.3618 | -2.732 | 42.2856 | -90.5632 | -79.3063
936 | 0.078 | 36.2062 | 1.5054 | 31.0648 | -0.0026506 | 5.1415 | -24311.7942 | -32.7604 | -15.4159 | 49.1803 | -4.6521 | -2.1891 | 42.2933 | -90.5321 | -79.3462
937 | 0.078083 | 34.1657 | 1.5028 | 29.8834 | -0.0028525 | 4.2823 | -24655.9065 | -31.3558 | -13.5689 | 49.1683 | -3.9301 | -1.7007 | 42.2995 | -90.5005 | -79.3838
938 | 0.078167 | 32.0976 | 1.4999 | 28.6601 | -0.0030636 | 3.4375 | -24975.8763 | -29.8436 | -11.8159 | 49.1572 | -3.1961 | -1.2654 | 42.3046 | -90.4687 | -79.4191
939 | 0.07825 | 30.0038 | 1.4969 | 27.3995 | -0.0032854 | 2.6043 | -25271.3874 | -28.23 | -10.1634 | 49.1471 | -2.4503 | -0.88217 | 42.3086 | -90.4365 | -79.4522
940 | 0.078333 | 27.8864 | 1.4936 | 26.1065 | -0.0035193 | 1.7799 | -25542.1476 | -26.5215 | -8.6174 | 49.1378 | -1.6928 | -0.55001 | 42.3116 | -90.404 | -79.4831
941 | 0.078417 | 25.7474 | 1.4901 | 24.7861 | -0.0037669 | 0.9613 | -25787.8892 | -24.7251 | -7.1833 | 49.1294 | -0.92313 | -0.26819 | 42.3137 | -90.3712 | -79.5118
942 | 0.0785 | 23.5891 | 1.4863 | 23.4436 | -0.0040302 | 0.1455 | -26008.3692 | -22.848 | -5.8664 | 49.122 | -0.14093 | -0.036185 | 42.315 | -90.3383 | -79.5383
943 | 0.078583 | 21.4134 | 1.4823 | 22.0842 | -0.0043112 | -0.67073 | -26203.3695 | -20.8977 | -4.6712 | 49.1155 | 0.65458 | 0.14632 | 42.3157 | -90.3052 | -79.5626
944 | 0.078667 | 19.2226 | 1.4779 | 20.7134 | -0.0046121 | -1.4908 | -26372.6972 | -18.8821 | -3.602 | 49.1099 | 1.4644 | 0.27935 | 42.3158 | -90.2719 | -79.5847
945 | 0.07875 | 17.0187 | 1.4733 | 19.337 | -0.0049354 | -2.3183 | -26516.1847 | -16.8092 | -2.6623 | 49.1052 | 2.2897 | 0.36266 | 42.3155 | -90.2385 | -79.6047
946 | 0.078833 | 14.8039 | 1.4684 | 17.9609 | -0.0052838 | -3.157 | -26633.6899 | -14.6872 | -1.8554 | 49.1015 | 3.1321 | 0.39568 | 42.3147 | -90.2051 | -79.6224
947 | 0.078917 | 12.5805 | 1.4631 | 16.5915 | -0.0056604 | -4.0111 | -26725.0964 | -12.5246 | -1.1839 | 49.0987 | 3.9933 | 0.37748 | 42.3137 | -90.1716 | -79.638
948 | 0.079 | 10.3505 | 1.4575 | 15.2353 | -0.0060684 | -4.8848 | -26790.3134 | -10.3301 | -0.64991 | 49.0968 | 4.8752 | 0.30672 | 42.3126 | -90.1381 | -79.6513
949 | 0.079083 | 8.1161 | 1.4514 | 13.8991 | -0.0065112 | -5.7829 | -26829.2761 | -8.1121 | -0.25493 | 49.0958 | 5.7801 | 0.18165 | 42.3113 | -90.1046 | -79.6625
950 | 0.079167 | 5.8797 | 1.4449 | 12.59 | -0.0069924 | -6.7104 | -26841.9456 | -5.8797 | -3.8174e-14 | 49.0958 | 6.7104 | 4.3567e-14 | 42.3101 | -90.0713 | -79.6713
951 | 0.07925 | 3.6432 | 1.4379 | 11.3156 | -0.0075154 | -7.6723 | -26828.3089 | -3.6414 | 0.11444 | 49.0966 | 7.6685 | -0.24099 | 42.3091 | -90.038 | -79.6779
952 | 0.079333 | 1.409 | 1.4304 | 10.0834 | -0.0080836 | -8.6744 | -26788.379 | -1.4062 | 0.088473 | 49.0984 | 8.6573 | -0.54467 | 42.3083 | -90.0048 | -79.6821
953 | 0.079417 | -0.82078 | 1.4223 | 8.9014 | -0.0086998 | -9.7222 | -26722.1948 | 0.81714 | -0.077242 | 49.1011 | 9.679 | -0.91494 | 42.3079 | -89.9719 | -79.684
954 | 0.0795 | -3.044 | 1.4136 | 7.7774 | -0.0093658 | -10.8214 | -26629.8212 | 3.02 | -0.38151 | 49.1047 | 10.736 | -1.3563 | 42.308 | -89.9391 | -79.6835
955 | 0.079583 | -5.2584 | 1.4042 | 6.7192 | -0.010082 | -11.9776 | -26511.3487 | 5.1936 | -0.82259 | 49.1091 | 11.8301 | -1.8737 | 42.3088 | -89.9066 | -79.6806
956 | 0.079667 | -7.4618 | 1.3941 | 5.7342 | -0.010848 | -13.196 | -26366.894 | 7.3296 | -1.3982 | 49.1145 | 12.9622 | -2.4727 | 42.3103 | -89.8743 | -79.6752
957 | 0.07975 | -9.6521 | 1.3833 | 4.8288 | -0.011658 | -14.4809 | -26196.5989 | 9.4197 | -2.1055 | 49.1206 | 14.1322 | -3.1589 | 42.3128 | -89.8423 | -79.6674
958 | 0.079833 | -11.8272 | 1.3716 | 4.0084 | -0.012507 | -15.8356 | -26000.6313 | 11.4556 | -2.9413 | 49.1277 | 15.3381 | -3.9381 | 42.3162 | -89.8107 | -79.6572
959 | 0.079917 | -13.9849 | 1.3591 | 3.2768 | -0.013385 | -17.2616 | -25779.1839 | 13.4296 | -3.9016 | 49.1356 | 16.5762 | -4.8158 | 42.3209 | -89.7795 | -79.6446
960 | 0.08 | -16.123 | 1.3457 | 2.6357 | -0.014277 | -18.7587 | -25532.4748 | 15.3339 | -4.9823 | 49.1443 | 17.8406 | -5.7967 | 42.3268 | -89.7486 | -79.6298
961 | 0.080083 | -18.2396 | 1.3315 | 2.0844 | -0.01517 | -20.324 | -25260.7471 | 17.1613 | -6.1784 | 49.1538 | 19.1224 | -6.8845 | 42.334 | -89.7182 | -79.6129
962 | 0.080167 | -20.3324 | 1.3163 | 1.6199 | -0.016049 | -21.9524 | -24964.2684 | 18.9046 | -7.4849 | 49.1642 | 20.4108 | -8.0812 | 42.3427 | -89.6882 | -79.5941
963 | 0.08025 | -22.3996 | 1.3002 | 1.2368 | -0.016898 | -23.6364 | -24643.3309 | 20.5573 | -8.896 | 49.1753 | 21.6924 | -9.3871 | 42.3528 | -89.6587 | -79.5737
964 | 0.080333 | -24.439 | 1.2833 | 0.92748 | -0.017704 | -25.3665 | -24298.2508 | 22.1131 | -10.4056 | 49.1872 | 22.9523 | -10.8005 | 42.3644 | -89.6297 | -79.5519
965 | 0.080417 | -26.4486 | 1.2656 | 0.68325 | -0.01846 | -27.1319 | -23929.3683 | 23.5659 | -12.0074 | 49.1999 | 24.1747 | -12.3176 | 42.3774 | -89.6012 | -79.529
966 | 0.0805 | -28.4266 | 1.2472 | 0.49453 | -0.019159 | -28.9211 | -23537.0468 | 24.9104 | -13.6946 | 49.2133 | 25.3438 | -13.9329 | 42.3916 | -89.5734 | -79.5054
967 | 0.080583 | -30.3708 | 1.228 | 0.35179 | -0.019801 | -30.7226 | -23121.6731 | 26.1415 | -15.46 | 49.2274 | 26.4443 | -15.6391 | 42.4072 | -89.5461 | -79.4813
968 | 0.080667 | -32.2796 | 1.2082 | 0.24602 | -0.020386 | -32.5256 | -22683.6567 | 27.2545 | -17.2963 | 49.2422 | 27.4623 | -17.4281 | 42.4238 | -89.5194 | -79.4572
969 | 0.08075 | -34.1508 | 1.1878 | 0.16919 | -0.020917 | -34.32 | -22223.4293 | 28.2455 | -19.1956 | 49.2577 | 28.3854 | -19.2907 | 42.4415 | -89.4934 | -79.4331
970 | 0.080833 | -35.9829 | 1.1669 | 0.11445 | -0.021399 | -36.0973 | -21741.4448 | 29.1107 | -21.1502 | 49.2738 | 29.2033 | -21.2175 | 42.4601 | -89.468 | -79.4093
971 | 0.080917 | -37.7738 | 1.1455 | 0.076171 | -0.021837 | -37.85 | -21238.1783 | 29.8472 | -23.1518 | 49.2906 | 29.9074 | -23.1985 | 42.4796 | -89.4433 | -79.386
972 | 0.081 | -39.522 | 1.1237 | 0.049877 | -0.022233 | -39.5719 | -20714.126 | 30.4522 | -25.1923 | 49.308 | 30.4906 | -25.2241 | 42.4997 | -89.4193 | -79.3634
973 | 0.081083 | -41.2256 | 1.1014 | 0.032134 | -0.022593 | -41.2577 | -20169.8046 | 30.9238 | -27.263 | 49.3261 | 30.9479 | -27.2842 | 42.5205 | -89.3961 | -79.3415
974 | 0.081167 | -42.8831 | 1.0789 | 0.020368 | -0.022918 | -42.9034 | -19605.751 | 31.2604 | -29.3555 | 49.3447 | 31.2753 | -29.3694 | 42.5419 | -89.3735 | -79.3205
975 | 0.08125 | -44.4927 | 1.0559 | 0.0127 | -0.023212 | -44.5054 | -19022.5211 | 31.4611 | -31.4611 | 49.3638 | 31.4701 | -31.4701 | 42.5639 | -89.3518 | -79.3003
976 | 0.081333 | -46.053 | 1.0327 | 0.0077877 | -0.023477 | -46.0608 | -18420.6903 | 31.5254 | -33.5712 | 49.3835 | 31.5308 | -33.5768 | 42.5863 | -89.3308 | -79.2811
977 | 0.081417 | -47.5623 | 1.0092 | 0.0046957 | -0.023713 | -47.567 | -17800.852 | 31.4535 | -35.677 | 49.4037 | 31.4566 | -35.6805 | 42.6091 | -89.3107 | -79.2629
978 | 0.0815 | -49.0193 | 0.98553 | 0.0027832 | -0.023921 | -49.0221 | -17163.6174 | 31.2461 | -37.77 | 49.4244 | 31.2478 | -37.7722 | 42.6323 | -89.2913 | -79.2457
979 | 0.081583 | -50.4225 | 0.96161 | 0.001621 | -0.024102 | -50.4241 | -16509.615 | 30.9043 | -39.8416 | 49.4456 | 30.9053 | -39.8428 | 42.6559 | -89.2728 | -79.2295
980 | 0.081667 | -51.7704 | 0.93751 | 0.00092736 | -0.024257 | -51.7714 | -15839.4897 | 30.4299 | -41.8832 | 49.4671 | 30.4305 | -41.8839 | 42.6798 | -89.2551 | -79.2144
981 | 0.08175 | -53.0619 | 0.91325 | 0.00052093 | -0.024385 | -53.0625 | -15153.9024 | 29.8252 | -43.8865 | 49.4892 | 29.8255 | -43.8869 | 42.704 | -89.2382 | -79.2003
982 | 0.081833 | -54.2957 | 0.88887 | 0.00028721 | -0.024488 | -54.296 | -14453.5293 | 29.0931 | -45.8434 | 49.5116 | 29.0932 | -45.8436 | 42.7285 | -89.2223 | -79.1874
983 | 0.081917 | -55.4705 | 0.86438 | 0.00015534 | -0.024564 | -55.4706 | -13739.0612 | 28.2368 | -47.7458 | 49.5343 | 28.2368 | -47.7459 | 42.7532 | -89.2072 | -79.1755
984 | 0.082 | -56.5852 | 0.83982 | 8.2382e-05 | -0.024614 | -56.5852 | -13011.2026 | 27.2601 | -49.586 | 49.5574 | 27.2601 | -49.586 | 42.7781 | -89.193 | -79.1646
985 | 0.082083 | -57.6387 | 0.8152 | 4.2818e-05 | -0.024638 | -57.6387 | -12270.6714 | 26.1674 | -51.3564 | 49.5809 | 26.1674 | -51.3565 | 42.8031 | -89.1797 | -79.1549
986 | 0.082167 | -58.6299 | 0.79057 | 2.1798e-05 | -0.024635 | -58.63 | -11518.1981 | 24.9634 | -53.05 | 49.6046 | 24.9634 | -53.05 | 42.8283 | -89.1672 | -79.1463
987 | 0.08225 | -59.558 | 0.76593 | 1.0863e-05 | -0.024607 | -59.5581 | -10754.5247 | 23.6534 | -54.6597 | 49.6286 | 23.6534 | -54.6597 | 42.8537 | -89.1557 | -79.1387
988 | 0.082333 | -60.4221 | 0.74132 | 5.2959e-06 | -0.024553 | -60.4221 | -9980.4045 | 22.2428 | -56.179 | 49.6528 | 22.2429 | -56.179 | 42.8791 | -89.1451 | -79.1323
989 | 0.082417 | -61.2212 | 0.71677 | 2.5242e-06 | -0.024473 | -61.2212 | -9196.6011 | 20.7379 | -57.6018 | 49.6772 | 20.7379 | -57.6018 | 42.9047 | -89.1355 | -79.1269
990 | 0.0825 | -61.9546 | 0.6923 | 1.1755e-06 | -0.024367 | -61.9546 | -8403.8874 | 19.145 | -58.9223 | 49.7018 | 19.145 | -58.9223 | 42.9302 | -89.1267 | -79.1227
991 | 0.082583 | -62.6216 | 0.66793 | 5.3439e-07 | -0.024235 | -62.6216 | -7603.0455 | 17.4709 | -60.1351 | 49.7266 | 17.4709 | -60.1351 | 42.9558 | -89.1189 | -79.1195
992 | 0.082667 | -63.2216 | 0.6437 | 2.37e-07 | -0.024078 | -63.2216 | -6794.8651 | 15.7226 | -61.2353 | 49.7515 | 15.7226 | -61.2353 | 42.9814 | -89.112 | -79.1174
993 | 0.08275 | -63.7539 | 0.61962 | 1.0245e-07 | -0.023895 | -63.7539 | -5980.1435 | 13.9075 | -62.2185 | 49.7766 | 13.9075 | -62.2185 | 43.0069 | -89.106 | -79.1164
994 | 0.082833 | -64.2181 | 0.59572 | 4.3126e-08 | -0.023687 | -64.2181 | -5159.6842 | 12.0333 | -63.0806 | 49.8017 | 12.0333 | -63.0806 | 43.0324 | -89.101 | -79.1164
995 | 0.082917 | -64.6137 | 0.57204 | 1.7664e-08 | -0.023454 | -64.6137 | -4334.2964 | 10.1078 | -63.8182 | 49.8268 | 10.1078 | -63.8182 | 43.0578 | -89.0969 | -79.1175
996 | 0.083 | -64.9404 | 0.54858 | 7.032e-09 | -0.023196 | -64.9404 | -3504.7945 | 8.1392 | -64.4283 | 49.8521 | 8.1392 | -64.4283 | 43.0832 | -89.0937 | -79.1197
997 | 0.083083 | -65.1977 | 0.52539 | 2.7182e-09 | -0.022914 | -65.1977 | -2671.9964 | 6.1357 | -64.9084 | 49.8773 | 6.1357 | -64.9084 | 43.1083 | -89.0914 | -79.1229
998 | 0.083167 | -65.3856 | 0.50247 | 1.0191e-09 | -0.022607 | -65.3856 | -1836.7237 | 4.1056 | -65.2566 | 49.9025 | 4.1056 | -65.2566 | 43.1334 | -89.09 | -79.1271
999 | 0.08325 | -65.5038 | 0.47986 | 3.7015e-10 | -0.022277 | -65.5038 | -999.8003 | 2.0575 | -65.4715 | 49.9276 | 2.0575 | -65.4715 | 43.1582 | -89.0896 | -79.1324
1000 | 0.083333 | -65.5522 | 0.45759 | 1.3008e-10 | -0.021922 | -65.5522 | -162.0517 | 3.1317e-13 | -65.5522 | 49.9527 | 3.1317e-13 | -65.5522 | 43.1829 | -89.09 | -79.1387
1001 | 0.083417 | -65.5308 | 0.43567 | 4.4171e-11 | -0.021545 | -65.5308 | 675.6959 | -2.0584 | -65.4985 | 49.9777 | -2.0584 | -65.4985 | 43.2073 | -89.0914 | -79.146
1002 | 0.0835 | -65.4396 | 0.41412 | 1.4473e-11 | -0.021144 | -65.4396 | 1512.616 | -4.109 | -65.3105 | 50.0026 | -4.109 | -65.3105 | 43.2315 | -89.0936 | -79.1542
1003 | 0.083583 | -65.2788 | 0.39298 | 4.569e-12 | -0.020722 | -65.2788 | 2347.8831 | -6.1433 | -64.9891 | 50.0274 | -6.1433 | -64.9891 | 43.2554 | -89.0968 | -79.1635
1004 | 0.083667 | -65.0484 | 0.37225 | 1.3875e-12 | -0.020277 | -65.0484 | 3180.6734 | -8.1527 | -64.5355 | 50.052 | -8.1527 | -64.5355 | 43.279 | -89.1008 | -79.1736
1005 | 0.08375 | -64.7488 | 0.35198 | 4.0468e-13 | -0.01981 | -64.7488 | 4010.1654 | -10.1289 | -63.9516 | 50.0764 | -10.1289 | -63.9516 | 43.3023 | -89.1056 | -79.1848
1006 | 0.083833 | -64.3802 | 0.33217 | 1.1315e-13 | -0.019322 | -64.3802 | 4835.5408 | -12.0636 | -63.2398 | 50.1006 | -12.0636 | -63.2398 | 43.3253 | -89.1114 | -79.1968
1007 | 0.083917 | -63.943 | 0.31285 | 3.0271e-14 | -0.018814 | -63.943 | 5655.9857 | -13.9487 | -62.403 | 50.1245 | -13.9487 | -62.403 | 43.3479 | -89.1179 | -79.2097
1008 | 0.084 | -63.4376 | 0.29403 | 7.7347e-15 | -0.018285 | -63.4376 | 6470.6907 | -15.7763 | -61.4446 | 50.1482 | -15.7763 | -61.4446 | 43.3701 | -89.1253 | -79.2235
1009 | 0.084083 | -62.8647 | 0.27575 | 1.8836e-15 | -0.017737 | -62.8647 | 7278.8522 | -17.5387 | -60.3686 | 50.1717 | -17.5387 | -60.3686 | 43.392 | -89.1336 | -79.2382
1010 | 0.084167 | -62.2247 | 0.25801 | 4.3627e-16 | -0.01717 | -62.2247 | 8079.673 | -19.2285 | -59.1792 | 50.1948 | -19.2285 | -59.1792 | 43.4134 | -89.1426 | -79.2538
1011 | 0.08425 | -61.5183 | 0.24084 | 9.5896e-17 | -0.016584 | -61.5183 | 8872.3633 | -20.8386 | -57.8814 | 50.2176 | -20.8386 | -57.8814 | 43.4344 | -89.1524 | -79.2701
1012 | 0.084333 | -60.7462 | 0.22426 | 1.996e-17 | -0.01598 | -60.7462 | 9656.1413 | -22.3622 | -56.4804 | 50.2401 | -22.3622 | -56.4804 | 43.455 | -89.163 | -79.2873
1013 | 0.084417 | -59.9092 | 0.20828 | 3.9252e-18 | -0.015359 | -59.9092 | 10430.2337 | -23.7928 | -54.982 | 50.2622 | -23.7928 | -54.982 | 43.475 | -89.1744 | -79.3052
1014 | 0.0845 | -59.0081 | 0.19292 | 7.2774e-19 | -0.014721 | -59.0081 | 11193.877 | -25.1244 | -53.3922 | 50.284 | -25.1244 | -53.3922 | 43.4946 | -89.1864 | -79.3239
1015 | 0.084583 | -58.0439 | 0.1782 | 1.2694e-19 | -0.014067 | -58.0439 | 11946.3181 | -26.3514 | -51.7175 | 50.3053 | -26.3514 | -51.7175 | 43.5137 | -89.1993 | -79.3433
1016 | 0.084667 | -57.0174 | 0.16413 | 2.0795e-20 | -0.013397 | -57.0174 | 12686.8149 | -27.4684 | -49.9648 | 50.3262 | -27.4684 | -49.9648 | 43.5323 | -89.2128 | -79.3634
1017 | 0.08475 | -55.9298 | 0.15073 | 3.1946e-21 | -0.012713 | -55.9298 | 13414.6368 | -28.4706 | -48.1411 | 50.3467 | -28.4706 | -48.1411 | 43.5504 | -89.227 | -79.3842
1018 | 0.084833 | -54.782 | 0.13802 | 4.5982e-22 | -0.012014 | -54.782 | 14129.0661 | -29.3537 | -46.254 | 50.3668 | -29.3537 | -46.254 | 43.5679 | -89.2419 | -79.4057
1019 | 0.084917 | -53.5753 | 0.12601 | 6.2009e-23 | -0.011302 | -53.5753 | 14829.3981 | -30.1138 | -44.3111 | 50.3863 | -30.1138 | -44.3111 | 43.5848 | -89.2575 | -79.4278
1020 | 0.085 | -52.3109 | 0.1147 | 7.8443e-24 | -0.010578 | -52.3109 | 15514.942 | -30.7476 | -42.3204 | 50.4054 | -30.7476 | -42.3204 | 43.6012 | -89.2737 | -79.4506
1021 | 0.085083 | -50.9899 | 0.10413 | 9.3357e-25 | -0.0098413 | -50.9899 | 16185.0217 | -31.2521 | -40.2899 | 50.424 | -31.2521 | -40.2899 | 43.617 | -89.2905 | -79.4739
1022 | 0.085167 | -49.6138 | 0.094286 | 1.0509e-25 | -0.0090935 | -49.6138 | 16838.9764 | -31.625 | -38.2281 | 50.4421 | -31.625 | -38.2281 | 43.6322 | -89.3079 | -79.4978
1023 | 0.08525 | -48.1839 | 0.085192 | 1.1286e-26 | -0.0083351 | -48.1839 | 17476.1609 | -31.8646 | -36.1433 | 50.4596 | -31.8646 | -36.1433 | 43.6468 | -89.3259 | -79.5222
1024 | 0.085333 | -46.7016 | 0.076857 | 1.1717e-27 | -0.007567 | -46.7016 | 18095.947 | -31.9694 | -34.044 | 50.4766 | -31.9694 | -34.044 | 43.6608 | -89.3444 | -79.5471
1025 | 0.085417 | -45.1684 | 0.06929 | 1.1982e-28 | -0.0067899 | -45.1684 | 18697.7234 | -31.9389 | -31.9389 | 50.4931 | -31.9389 | -31.9389 | 43.6741 | -89.3635 | -79.5725
1026 | 0.0855 | -43.5858 | 0.0625 | 1.2392e-29 | -0.0060046 | -43.5858 | 19280.8965 | -31.7727 | -29.8366 | 50.5089 | -31.7727 | -29.8366 | 43.6868 | -89.3831 | -79.5984
1027 | 0.085583 | -41.9555 | 0.056495 | 1.343e-30 | -0.0052118 | -41.9555 | 19844.8913 | -31.4713 | -27.7456 | 50.5242 | -31.4713 | -27.7456 | 43.6988 | -89.4032 | -79.6246
1028 | 0.085667 | -40.2789 | 0.051284 | 1.597e-31 | -0.0044123 | -40.2789 | 20389.1515 | -31.0354 | -25.6747 | 50.5389 | -31.0354 | -25.6747 | 43.7102 | -89.4237 | -79.6513
1029 | 0.08575 | -38.5578 | 0.046871 | 2.2066e-32 | -0.003607 | -38.5578 | 20913.1404 | -30.4667 | -23.6324 | 50.553 | -30.4667 | -23.6324 | 43.721 | -89.4447 | -79.6784
1030 | 0.085833 | -36.794 | 0.043264 | 3.79e-33 | -0.0027965 | -36.794 | 21416.3414 | -29.7669 | -21.6269 | 50.5664 | -29.7669 | -21.6269 | 43.731 | -89.4661 | -79.7058
1031 | 0.085917 | -34.989 | 0.040468 | 8.7134e-34 | -0.0019819 | -34.989 | 21898.2581 | -28.9387 | -19.6668 | 50.5792 | -28.9387 | -19.6668 | 43.7404 | -89.488 | -79.7335
1032 | 0.086 | -33.1448 | 0.038486 | 2.8868e-34 | -0.0011637 | -33.1448 | 22358.4153 | -27.9851 | -17.7599 | 50.5914 | -27.9851 | -17.7599 | 43.7491 | -89.5102 | -79.7615
1033 | 0.086083 | -31.2632 | 0.037322 | 1.4692e-34 | -0.00034288 | -31.2632 | 22796.3595 | -26.9096 | -15.9143 | 50.603 | -26.9096 | -15.9143 | 43.7571 | -89.5327 | -79.7897
1034 | 0.086167 | -29.3461 | 0.036979 | 1.1992e-34 | 0.00047978 | -29.3461 | 23211.6586 | -25.7162 | -14.1376 | 50.6139 | -25.7162 | -14.1376 | 43.7644 | -89.5556 | -79.8182
1035 | 0.08625 | -27.3953 | 0.037459 | 1.5924e-34 | 0.0013035 | -27.3953 | 23603.9034 | -24.4094 | -12.4372 | 50.6241 | -24.4094 | -12.4372 | 43.7711 | -89.5788 | -79.8469
1036 | 0.086333 | -25.4128 | 0.038763 | 3.3796e-34 | 0.0021273 | -25.4128 | 23972.707 | -22.9941 | -10.8202 | 50.6337 | -22.9941 | -10.8202 | 43.777 | -89.6022 | -79.8758
1037 | 0.086417 | -23.4005 | 0.04089 | 1.0948e-33 | 0.0029506 | -23.4005 | 24317.7059 | -21.4759 | -9.2935 | 50.6426 | -21.4759 | -9.2935 | 43.7822 | -89.626 | -79.9048
1038 | 0.0865 | -21.3605 | 0.043841 | 5.0705e-33 | 0.0037725 | -21.3605 | 24638.56 | -19.8605 | -7.8633 | 50.6508 | -19.8605 | -7.8633 | 43.7868 | -89.6499 | -79.9339
1039 | 0.086583 | -19.2947 | 0.047613 | 3.1171e-32 | 0.0045921 | -19.2947 | 24934.953 | -18.154 | -6.5359 | 50.6584 | -18.154 | -6.5359 | 43.7906 | -89.6741 | -79.9632
1040 | 0.086667 | -17.2053 | 0.052205 | 2.363e-31 | 0.0054086 | -17.2053 | 25206.5928 | -16.3632 | -5.3167 | 50.6653 | -16.3632 | -5.3167 | 43.7938 | -89.6984 | -79.9925
1041 | 0.08675 | -15.0943 | 0.057614 | 2.0671e-30 | 0.0062213 | -15.0943 | 25453.2117 | -14.495 | -4.2112 | 50.6714 | -14.495 | -4.2112 | 43.7962 | -89.723 | -80.0218
1042 | 0.086833 | -12.9638 | 0.063835 | 1.9728e-29 | 0.0070294 | -12.9638 | 25674.5667 | -12.5565 | -3.224 | 50.6769 | -12.5565 | -3.224 | 43.7979 | -89.7476 | -80.0511
1043 | 0.086917 | -10.8159 | 0.070865 | 1.9643e-28 | 0.0078319 | -10.8159 | 25870.4398 | -10.5555 | -2.3594 | 50.6817 | -10.5555 | -2.3594 | 43.799 | -89.7724 | -80.0804
1044 | 0.087 | -8.6528 | 0.078697 | 1.9714e-27 | 0.0086282 | -8.6528 | 26040.638 | -8.4995 | -1.6214 | 50.6858 | -8.4995 | -1.6214 | 43.7993 | -89.7972 | -80.1097
1045 | 0.087083 | -6.4766 | 0.087325 | 1.9444e-26 | 0.0094175 | -6.4766 | 26184.9937 | -6.3968 | -1.0132 | 50.6893 | -6.3968 | -1.0132 | 43.799 | -89.8222 | -80.1388
1046 | 0.087167 | -4.2894 | 0.096742 | 1.8506e-25 | 0.010199 | -4.2894 | 26303.3648 | -4.2555 | -0.5376 | 50.692 | -4.2555 | -0.5376 | 43.798 | -89.8471 | -80.1679
1047 | 0.08725 | -2.0934 | 0.10694 | 1.6786e-24 | 0.010972 | -2.0934 | 26395.6349 | -2.0841 | -0.19701 | 50.694 | -2.0841 | -0.19701 | 43.7962 | -89.8721 | -80.1969
1048 | 0.087333 | 0.10918 | 0.11791 | 1.4391e-23 | 0.011735 | 0.10918 | 26461.7133 | 0.10897 | 0.0068557 | 50.6954 | 0.10897 | 0.0068557 | 43.7939 | -89.8971 | -80.2256
1049 | 0.087417 | 2.3162 | 0.12965 | 1.1603e-22 | 0.012488 | 2.3162 | 26501.5352 | 2.315 | 0.072753 | 50.696 | 2.315 | 0.072753 | 43.7908 | -89.922 | -80.2543
1050 | 0.0875 | 4.5254 | 0.14214 | 8.7751e-22 | 0.013231 | 4.5254 | 26515.0616 | 4.5254 | 2.9935e-14 | 50.696 | 4.5254 | 2.9935e-14 | 43.7871 | -89.9469 | -80.2826
1051 | 0.087583 | 6.7346 | 0.15537 | 6.2178e-21 | 0.013961 | 6.7346 | 26502.2796 | 6.7313 | -0.21154 | 50.6953 | 6.7313 | -0.21154 | 43.7827 | -89.9717 | -80.3108
1052 | 0.087667 | 8.9417 | 0.16933 | 4.1286e-20 | 0.01468 | 8.9417 | 26463.2021 | 8.924 | -0.56145 | 50.6939 | 8.924 | -0.56145 | 43.7777 | -89.9964 | -80.3387
1053 | 0.08775 | 11.1444 | 0.18401 | 2.5714e-19 | 0.015385 | 11.1444 | 26397.8681 | 11.095 | -1.0488 | 50.6919 | 11.095 | -1.0488 | 43.772 | -90.021 | -80.3663
1054 | 0.087833 | 13.3406 | 0.19939 | 1.5045e-18 | 0.016077 | 13.3406 | 26306.3424 | 13.2354 | -1.672 | 50.6891 | 13.2354 | -1.672 | 43.7657 | -90.0454 | -80.3936
1055 | 0.087917 | 15.5281 | 0.21547 | 8.2847e-18 | 0.016754 | 15.5281 | 26188.7157 | 15.3369 | -2.4291 | 50.6858 | 15.3369 | -2.4291 | 43.7588 | -90.0697 | -80.4206
1056 | 0.088 | 17.7047 | 0.23222 | 4.3025e-17 | 0.017416 | 17.7047 | 26045.1045 | 17.3911 | -3.3175 | 50.6817 | 17.3911 | -3.3175 | 43.7512 | -90.0938 | -80.4472
1057 | 0.088083 | 19.8682 | 0.24964 | 2.1119e-16 | 0.018062 | 19.8682 | 25875.6508 | 19.3897 | -4.3341 | 50.6771 | 19.3897 | -4.3341 | 43.7431 | -90.1176 | -80.4734
1058 | 0.088167 | 22.0166 | 0.2677 | 9.82e-16 | 0.018692 | 22.0166 | 25680.5223 | 21.3249 | -5.4753 | 50.6717 | 21.3249 | -5.4753 | 43.7343 | -90.1412 | -80.4992
1059 | 0.08825 | 24.1476 | 0.28639 | 4.335e-15 | 0.019305 | 24.1476 | 25459.9119 | 23.1888 | -6.737 | 50.6658 | 23.1888 | -6.737 | 43.725 | -90.1646 | -80.5246
1060 | 0.088333 | 26.2592 | 0.3057 | 1.8207e-14 | 0.0199 | 26.2592 | 25214.0376 | 24.974 | -8.1145 | 50.6592 | 24.974 | -8.1145 | 43.7151 | -90.1877 | -80.5496
1061 | 0.088417 | 28.3492 | 0.3256 | 7.2913e-14 | 0.020477 | 28.3492 | 24943.1424 | 26.6733 | -9.603 | 50.6521 | 26.6733 | -9.603 | 43.7047 | -90.2105 | -80.5741
1062 | 0.0885 | 30.4157 | 0.34608 | 2.7897e-13 | 0.021035 | 30.4157 | 24647.4942 | 28.2798 | -11.1968 | 50.6443 | 28.2798 | -11.1968 | 43.6937 | -90.233 | -80.598
1063 | 0.088583 | 32.4565 | 0.36711 | 1.0217e-12 | 0.021574 | 32.4565 | 24327.3849 | 29.7871 | -12.89 | 50.6359 | 29.7871 | -12.89 | 43.6822 | -90.2551 | -80.6215
1064 | 0.088667 | 34.4696 | 0.38869 | 3.5886e-12 | 0.022093 | 34.4696 | 23983.1308 | 31.189 | -14.6764 | 50.627 | 31.189 | -14.6764 | 43.6701 | -90.2769 | -80.6444
1065 | 0.08875 | 36.453 | 0.41078 | 1.211e-11 | 0.022591 | 36.453 | 23615.0722 | 32.4799 | -16.5493 | 50.6174 | 32.4799 | -16.5493 | 43.6576 | -90.2983 | -80.6668
1066 | 0.088833 | 38.4048 | 0.43337 | 3.9323e-11 | 0.023069 | 38.4048 | 23223.5724 | 33.6544 | -18.5016 | 50.6074 | 33.6544 | -18.5016 | 43.6445 | -90.3193 | -80.6886
1067 | 0.088917 | 40.323 | 0.45644 | 1.2307e-10 | 0.023525 | 40.323 | 22809.0184 | 34.7077 | -20.5261 | 50.5968 | 34.7077 | -20.5261 | 43.631 | -90.3399 | -80.7098
1068 | 0.089 | 42.2056 | 0.47996 | 3.7182e-10 | 0.023959 | 42.2056 | 22371.8194 | 35.6354 | -22.6149 | 50.5856 | 35.6354 | -22.6149 | 43.6171 | -90.3601 | -80.7304
1069 | 0.089083 | 44.051 | 0.50392 | 1.0858e-09 | 0.024371 | 44.051 | 21912.4074 | 36.4337 | -24.7603 | 50.5739 | 36.4337 | -24.7603 | 43.6026 | -90.3798 | -80.7504
1070 | 0.089167 | 45.8571 | 0.52829 | 3.0691e-09 | 0.02476 | 45.8571 | 21431.236 | 37.0992 | -26.9541 | 50.5618 | 37.0992 | -26.9541 | 43.5878 | -90.399 | -80.7697
1071 | 0.08925 | 47.6223 | 0.55305 | 8.407e-09 | 0.025127 | 47.6223 | 20928.7806 | 37.629 | -29.188 | 50.5491 | 37.629 | -29.188 | 43.5726 | -90.4178 | -80.7884
1072 | 0.089333 | 49.3447 | 0.57818 | 2.2344e-08 | 0.025469 | 49.3447 | 20405.5372 | 38.0207 | -31.4535 | 50.536 | 38.0207 | -31.4535 | 43.5569 | -90.4361 | -80.8064
1073 | 0.089417 | 51.0226 | 0.60365 | 5.7681e-08 | 0.025788 | 51.0226 | 19862.0227 | 38.2726 | -33.7419 | 50.5224 | 38.2726 | -33.7419 | 43.5409 | -90.4538 | -80.8237
1074 | 0.0895 | 52.6545 | 0.62944 | 1.4479e-07 | 0.026083 | 52.6545 | 19298.7737 | 38.3834 | -36.0445 | 50.5084 | 38.3834 | -36.0445 | 43.5245 | -90.471 | -80.8404
1075 | 0.089583 | 54.2385 | 0.65552 | 3.5373e-07 | 0.026354 | 54.2385 | 18716.3465 | 38.3524 | -38.3524 | 50.4939 | 38.3524 | -38.3524 | 43.5078 | -90.4877 | -80.8563
1076 | 0.089667 | 55.7733 | 0.68188 | 8.4192e-07 | 0.0266 | 55.7733 | 18115.3162 | 38.1795 | -40.657 | 50.479 | 38.1795 | -40.657 | 43.4908 | -90.5039 | -80.8714
1077 | 0.08975 | 57.2573 | 0.70848 | 1.9539e-06 | 0.026821 | 57.2573 | 17496.2763 | 37.8649 | -42.9493 | 50.4638 | 37.8649 | -42.9493 | 43.4734 | -90.5194 | -80.8859
1078 | 0.089833 | 58.6889 | 0.7353 | 4.4252e-06 | 0.027017 | 58.6889 | 16859.8381 | 37.4097 | -45.2206 | 50.4481 | 37.4097 | -45.2206 | 43.4558 | -90.5344 | -80.8996
1079 | 0.089917 | 60.0668 | 0.76231 | 9.7879e-06 | 0.027187 | 60.0668 | 16206.6299 | 36.8154 | -47.4621 | 50.4321 | 36.8153 | -47.4621 | 43.4379 | -90.5488 | -80.9125
1080 | 0.09 | 61.3895 | 0.7895 | 2.116e-05 | 0.027332 | 61.3895 | 15537.2968 | 36.0839 | -49.6652 | 50.4158 | 36.0839 | -49.6652 | 43.4198 | -90.5625 | -80.9246
1081 | 0.090083 | 62.6559 | 0.81683 | 4.4738e-05 | 0.027451 | 62.6559 | 14852.4996 | 35.2178 | -51.8215 | 50.3991 | 35.2178 | -51.8214 | 43.4014 | -90.5757 | -80.936
1082 | 0.090167 | 63.8646 | 0.84428 | 9.2577e-05 | 0.027545 | 63.8645 | 14152.9146 | 34.2203 | -53.9226 | 50.3821 | 34.2203 | -53.9225 | 43.3828 | -90.5882 | -80.9466
1083 | 0.09025 | 65.0143 | 0.87183 | 0.0001876 | 0.027612 | 65.0141 | 13439.2324 | 33.095 | -55.9606 | 50.3648 | 33.0949 | -55.9604 | 43.3641 | -90.6001 | -80.9563
1084 | 0.090333 | 66.1041 | 0.89944 | 0.00037252 | 0.027653 | 66.1037 | 12712.1577 | 31.8459 | -57.9274 | 50.3473 | 31.8457 | -57.9271 | 43.3453 | -90.6114 | -80.9653
1085 | 0.090417 | 67.1327 | 0.92709 | 0.00072523 | 0.027668 | 67.1319 | 11972.4084 | 30.4776 | -59.8156 | 50.3295 | 30.4773 | -59.815 | 43.3264 | -90.622 | -80.9734
1086 | 0.0905 | 68.0991 | 0.95476 | 0.001385 | 0.027655 | 68.0977 | 11220.7149 | 28.9952 | -61.6179 | 50.3114 | 28.9946 | -61.6167 | 43.3076 | -90.6319 | -80.9806
1087 | 0.090583 | 69.0025 | 0.98242 | 0.0025958 | 0.027615 | 68.9999 | 10457.8193 | 27.4042 | -63.3273 | 50.2932 | 27.4032 | -63.325 | 43.289 | -90.6412 | -80.9869
1088 | 0.090667 | 69.8418 | 1.01 | 0.0047767 | 0.027545 | 69.837 | 9684.4749 | 25.7105 | -64.9373 | 50.2747 | 25.7087 | -64.9328 | 43.2708 | -90.6498 | -80.9923
1089 | 0.09075 | 70.6163 | 1.0376 | 0.0086338 | 0.027445 | 70.6076 | 8901.4452 | 23.9204 | -66.4415 | 50.2561 | 23.9175 | -66.4334 | 43.2533 | -90.6577 | -80.9967
1090 | 0.090833 | 71.3251 | 1.065 | 0.015334 | 0.027309 | 71.3098 | 8109.5033 | 22.0407 | -67.8342 | 50.2373 | 22.0359 | -67.8196 | 43.2371 | -90.665 | -81.0001
1091 | 0.090917 | 71.9676 | 1.0923 | 0.026764 | 0.027134 | 71.9409 | 7309.431 | 20.0783 | -69.1101 | 50.2184 | 20.0709 | -69.0844 | 43.223 | -90.6715 | -81.0025
1092 | 0.091 | 72.5432 | 1.1195 | 0.045919 | 0.026911 | 72.4972 | 6502.0183 | 18.0408 | -70.2641 | 50.1994 | 18.0293 | -70.2196 | 43.2118 | -90.6774 | -81.0039
1093 | 0.091083 | 73.0511 | 1.1464 | 0.077438 | 0.026629 | 72.9737 | 5688.0623 | 15.9356 | -71.2918 | 50.1802 | 15.9187 | -71.2162 | 43.2049 | -90.6825 | -81.0044
1094 | 0.091167 | 73.491 | 1.173 | 0.12834 | 0.026271 | 73.3627 | 4868.3667 | 13.7708 | -72.1893 | 50.161 | 13.7468 | -72.0632 | 43.204 | -90.687 | -81.0045
1095 | 0.09125 | 73.8624 | 1.1993 | 0.20892 | 0.025814 | 73.6535 | 4043.7406 | 11.5546 | -72.953 | 50.1417 | 11.5219 | -72.7467 | 43.2107 | -90.6907 | -81.0045
1096 | 0.091333 | 74.1649 | 1.2251 | 0.33378 | 0.025229 | 73.8311 | 3214.9983 | 9.2953 | -73.58 | 50.1223 | 9.2535 | -73.2489 | 43.2266 | -90.6938 | -81.0051
1097 | 0.091417 | 74.3981 | 1.2503 | 0.52267 | 0.024484 | 73.8755 | 2382.958 | 7.0015 | -74.0679 | 50.103 | 6.9523 | -73.5476 | 43.2532 | -90.6962 | -81.0073
1098 | 0.0915 | 74.5619 | 1.2748 | 0.80078 | 0.023545 | 73.7612 | 1548.441 | 4.6818 | -74.4148 | 50.0836 | 4.6315 | -73.6156 | 43.2911 | -90.6978 | -81.0121
1099 | 0.091583 | 74.6562 | 1.2983 | 1.1978 | 0.02239 | 73.4584 | 712.2713 | 2.345 | -74.6193 | 50.0643 | 2.3074 | -73.4221 | 43.3407 | -90.6988 | -81.0204
1100 | 0.091667 | 74.6806 | 1.3207 | 1.7448 | 0.021016 | 72.9359 | -124.7256 | 3.6592e-13 | -74.6806 | 50.045 | 3.5737e-13 | -72.9359 | 43.4015 | -90.6991 | -81.033
1101 | 0.09175 | 74.6354 | 1.3418 | 2.4693 | 0.019452 | 72.166 | -961.7233 | -2.3444 | -74.5985 | 50.0257 | -2.2668 | -72.1304 | 43.4726 | -90.6986 | -81.0508
1102 | 0.091833 | 74.5204 | 1.3612 | 3.3892 | 0.017756 | 71.1312 | -1797.8956 | -4.6792 | -74.3733 | 50.0065 | -4.4664 | -70.9908 | 43.5523 | -90.6975 | -81.0742
1103 | 0.091917 | 74.3358 | 1.379 | 4.5074 | 0.016006 | 69.8284 | -2632.4168 | -6.9956 | -74.0059 | 49.9874 | -6.5714 | -69.5185 | 43.6391 | -90.6957 | -81.1033
1104 | 0.092 | 74.0817 | 1.395 | 5.8101 | 0.014283 | 68.2716 | -3464.4631 | -9.2849 | -73.4975 | 49.9684 | -8.5567 | -67.7332 | 43.731 | -90.6932 | -81.138
1105 | 0.092083 | 73.7584 | 1.4093 | 7.2696 | 0.012649 | 66.4888 | -4293.2131 | -11.5384 | -72.8504 | 49.9495 | -10.4011 | -65.6702 | 43.8263 | -90.6901 | -81.1782
1106 | 0.092167 | 73.3663 | 1.4219 | 8.8489 | 0.011147 | 64.5174 | -5117.8486 | -13.7475 | -72.0668 | 49.9308 | -12.0894 | -63.3746 | 43.9234 | -90.6863 | -81.2233
1107 | 0.09225 | 72.9056 | 1.433 | 10.5075 | 0.0097934 | 62.3981 | -5937.5553 | -15.9039 | -71.1498 | 49.9123 | -13.6117 | -60.8954 | 44.0208 | -90.6818 | -81.273
1108 | 0.092333 | 72.3769 | 1.4428 | 12.2059 | 0.0085904 | 60.1709 | -6751.5241 | -17.9994 | -70.103 | 49.8939 | -14.9639 | -58.2805 | 44.1175 | -90.6766 | -81.3266
1109 | 0.092417 | 71.7805 | 1.4514 | 13.9088 | 0.0075286 | 57.8718 | -7558.9513 | -20.0261 | -68.9304 | 49.8757 | -16.1457 | -55.5739 | 44.2124 | -90.6708 | -81.3836
1110 | 0.0925 | 71.1172 | 1.459 | 15.5854 | 0.0065939 | 55.5318 | -8359.0399 | -21.9764 | -67.6365 | 49.8577 | -17.1603 | -52.8139 | 44.3049 | -90.6644 | -81.4435
1111 | 0.092583 | 70.3876 | 1.4656 | 17.2109 | 0.0057706 | 53.1767 | -9150.9998 | -23.8429 | -66.2263 | 49.84 | -18.013 | -50.0329 | 44.3944 | -90.6573 | -81.5058
1112 | 0.092667 | 69.5923 | 1.4713 | 18.7651 | 0.0050433 | 50.8272 | -9934.0491 | -25.6186 | -64.7053 | 49.8225 | -18.7108 | -47.258 | 44.4805 | -90.6496 | -81.5701
1113 | 0.09275 | 68.7322 | 1.4764 | 20.2323 | 0.0043982 | 48.4999 | -10707.4149 | -27.2968 | -63.0793 | 49.8053 | -19.2616 | -44.511 | 44.5628 | -90.6413 | -81.6357
1114 | 0.092833 | 67.808 | 1.4808 | 21.6006 | 0.0038229 | 46.2074 | -11470.3336 | -28.8713 | -61.3545 | 49.7884 | -19.6742 | -41.8097 | 44.6411 | -90.6324 | -81.7024
1115 | 0.092917 | 66.8208 | 1.4846 | 22.8613 | 0.0033067 | 43.9595 | -12222.0519 | -30.336 | -59.5377 | 49.7717 | -19.9572 | -39.1682 | 44.7154 | -90.6229 | -81.7698
1116 | 0.093 | 65.7714 | 1.4879 | 24.0081 | 0.0028408 | 41.7632 | -12961.8277 | -31.6856 | -57.6359 | 49.7554 | -20.1196 | -36.5974 | 44.7856 | -90.6128 | -81.8375
1117 | 0.093083 | 64.6608 | 1.4907 | 25.037 | 0.0024174 | 39.6238 | -13688.9306 | -32.915 | -55.6563 | 49.7394 | -20.1701 | -34.1059 | 44.8517 | -90.6022 | -81.9053
1118 | 0.093167 | 63.4902 | 1.4932 | 25.9456 | 0.0020302 | 37.5446 | -14402.6427 | -34.0198 | -53.6066 | 49.7237 | -20.1174 | -31.7 | 44.9137 | -90.591 | -81.9728
1119 | 0.09325 | 62.2608 | 1.4952 | 26.7329 | 0.0016736 | 35.5279 | -15102.2594 | -34.9957 | -51.4947 | 49.7084 | -19.9696 | -29.3844 | 44.9717 | -90.5793 | -82.0398
1120 | 0.093333 | 60.9736 | 1.4969 | 27.399 | 0.001343 | 33.5746 | -15787.0899 | -35.8394 | -49.3287 | 49.6935 | -19.7347 | -27.1624 | 45.0257 | -90.567 | -82.1061
1121 | 0.093417 | 59.63 | 1.4982 | 27.9449 | 0.0010344 | 31.6851 | -16456.4581 | -36.5477 | -47.117 | 49.6789 | -19.42 | -25.0361 | 45.076 | -90.5543 | -82.1714
1122 | 0.0935 | 58.2313 | 1.4992 | 28.3725 | 0.00074446 | 29.8588 | -17109.703 | -37.118 | -44.868 | 49.6648 | -19.0327 | -23.0066 | 45.1225 | -90.541 | -82.2357
1123 | 0.093583 | 56.7789 | 1.5 | 28.6841 | 0.00047012 | 28.0948 | -17746.1798 | -37.5485 | -42.5905 | 49.651 | -18.5794 | -21.0742 | 45.1655 | -90.5273 | -82.2988
1124 | 0.093667 | 55.2741 | 1.5004 | 28.8825 | 0.00020882 | 26.3916 | -18365.2599 | -37.8377 | -40.2931 | 49.6377 | -18.0663 | -19.2386 | 45.2051 | -90.5131 | -82.3605
1125 | 0.09375 | 53.7185 | 1.5007 | 28.9711 | -4.175e-05 | 24.7474 | -18966.3321 | -37.9847 | -37.9847 | 49.6248 | -17.4991 | -17.4991 | 45.2414 | -90.4984 | -82.4207
1126 | 0.093833 | 52.1136 | 1.5006 | 28.9533 | -0.00028365 | 23.1602 | -19548.803 | -37.9891 | -35.6742 | 49.6123 | -16.8831 | -15.8543 | 45.2747 | -90.4834 | -82.4794
1127 | 0.093917 | 50.4609 | 1.5003 | 28.8332 | -0.00051874 | 21.6277 | -20112.0973 | -37.8513 | -33.3704 | 49.6003 | -16.2232 | -14.3027 | 45.3049 | -90.4679 | -82.5364
1128 | 0.094 | 48.7621 | 1.4998 | 28.6147 | -0.00074874 | 20.1474 | -20655.6589 | -37.5718 | -31.0821 | 49.5888 | -15.5239 | -12.8425 | 45.3324 | -90.452 | -82.5916
1129 | 0.094083 | 47.0188 | 1.4991 | 28.302 | -0.00097524 | 18.7168 | -21178.951 | -37.1522 | -28.8182 | 49.5777 | -14.7892 | -11.4717 | 45.3573 | -90.4358 | -82.6451
1130 | 0.094167 | 45.2328 | 1.4981 | 27.8997 | -0.0011998 | 17.3331 | -21681.4569 | -36.5941 | -26.5872 | 49.5671 | -14.0228 | -10.1882 | 45.3796 | -90.4192 | -82.6967
1131 | 0.09425 | 43.4059 | 1.4969 | 27.4123 | -0.0014238 | 15.9936 | -22162.6805 | -35.9001 | -24.3977 | 49.557 | -13.228 | -8.9897 | 45.3996 | -90.4022 | -82.7464
1132 | 0.094333 | 41.5397 | 1.4955 | 26.8443 | -0.0016487 | 14.6953 | -22622.1464 | -35.0731 | -22.2581 | 49.5473 | -12.4077 | -7.8741 | 45.4174 | -90.385 | -82.7943
1133 | 0.094417 | 39.6361 | 1.4938 | 26.2007 | -0.0018759 | 13.4354 | -23059.401 | -34.1165 | -20.1764 | 49.5382 | -11.5644 | -6.8392 | 45.4332 | -90.3674 | -82.8401
1134 | 0.0945 | 37.6971 | 1.4919 | 25.4864 | -0.0021069 | 12.2107 | -23474.0124 | -33.0342 | -18.1607 | 49.5296 | -10.7003 | -5.8825 | 45.447 | -90.3495 | -82.884
1135 | 0.094583 | 35.7244 | 1.4898 | 24.7062 | -0.0023431 | 11.0182 | -23865.5712 | -31.8307 | -16.2185 | 49.5215 | -9.8173 | -5.0022 | 45.459 | -90.3314 | -82.9259
1136 | 0.094667 | 33.7201 | 1.4875 | 23.8653 | -0.0025861 | 9.8548 | -24233.6907 | -30.5109 | -14.3573 | 49.5139 | -8.9169 | -4.196 | 45.4694 | -90.3131 | -82.9658
1137 | 0.09475 | 31.6861 | 1.4849 | 22.969 | -0.0028375 | 8.7172 | -24578.0072 | -29.0801 | -12.5841 | 49.5069 | -8.0002 | -3.462 | 45.4783 | -90.2945 | -83.0037
1138 | 0.094833 | 29.6245 | 1.4821 | 22.0225 | -0.003099 | 7.6019 | -24898.1807 | -27.5441 | -10.9055 | 49.5004 | -7.0681 | -2.7985 | 45.4857 | -90.2757 | -83.0396
1139 | 0.094917 | 27.5371 | 1.479 | 21.0314 | -0.0033724 | 6.5057 | -25193.8949 | -25.9091 | -9.3279 | 49.4944 | -6.1211 | -2.2037 | 45.4918 | -90.2567 | -83.0735
1140 | 0.095 | 25.4262 | 1.4756 | 20.0012 | -0.0036598 | 5.4249 | -25464.8577 | -24.1817 | -7.8571 | 49.4889 | -5.1594 | -1.6764 | 45.4968 | -90.2376 | -83.1054
1141 | 0.095083 | 23.2937 | 1.4719 | 18.9378 | -0.0039633 | 4.3558 | -25710.8014 | -22.3688 | -6.4987 | 49.484 | -4.1829 | -1.2152 | 45.5007 | -90.2183 | -83.1352
1142 | 0.095167 | 21.1417 | 1.468 | 17.8472 | -0.0042853 | 3.2946 | -25931.4829 | -20.4775 | -5.2577 | 49.4797 | -3.1911 | -0.81933 | 45.5036 | -90.199 | -83.163
1143 | 0.09525 | 18.9725 | 1.4637 | 16.7354 | -0.0046284 | 2.237 | -26126.6843 | -18.5155 | -4.1387 | 49.4758 | -2.1832 | -0.48799 | 45.5057 | -90.1795 | -83.1887
1144 | 0.095333 | 16.788 | 1.4591 | 15.609 | -0.0049953 | 1.179 | -26296.2125 | -16.4906 | -3.1458 | 49.4726 | -1.1581 | -0.22091 | 45.507 | -90.1599 | -83.2125
1145 | 0.095417 | 14.5905 | 1.4541 | 14.4747 | -0.0053891 | 0.1158 | -26439.8999 | -14.4108 | -2.2825 | 49.4698 | -0.11437 | -0.018115 | 45.5077 | -90.1403 | -83.2341
1146 | 0.0955 | 12.3821 | 1.4487 | 13.3393 | -0.005813 | -0.9572 | -26557.6046 | -12.2844 | -1.5519 | 49.4676 | 0.94965 | 0.11997 | 45.5078 | -90.1206 | -83.2537
1147 | 0.095583 | 10.1649 | 1.4429 | 12.21 | -0.0062703 | -2.0451 | -26649.21 | -10.1198 | -0.9566 | 49.466 | 2.036 | 0.19246 | 45.5075 | -90.1009 | -83.2712
1148 | 0.095667 | 7.9413 | 1.4366 | 11.0944 | -0.0067644 | -3.1532 | -26714.6254 | -7.9256 | -0.49864 | 49.4649 | 3.1469 | 0.19799 | 45.5068 | -90.0812 | -83.2866
1149 | 0.09575 | 5.7132 | 1.4298 | 10.0002 | -0.0072988 | -4.287 | -26753.786 | -5.7104 | -0.17946 | 49.4644 | 4.2849 | 0.13466 | 45.5059 | -90.0615 | -83.2999
1150 | 0.095833 | 3.483 | 1.4225 | 8.9354 | -0.0078765 | -5.4523 | -26766.6529 | -3.483 | -3.5841e-14 | 49.4643 | 5.4523 | 5.6105e-14 | 45.5048 | -90.0419 | -83.311
1151 | 0.095917 | 1.2528 | 1.4147 | 7.9079 | -0.0085001 | -6.6551 | -26753.2131 | -1.2522 | 0.039353 | 49.4649 | 6.6518 | -0.20904 | 45.5038 | -90.0223 | -83.3199
1152 | 0.096 | -0.97511 | 1.4062 | 6.926 | -0.0091713 | -7.9011 | -26713.4795 | 0.97319 | -0.061228 | 49.4659 | 7.8855 | -0.49611 | 45.5028 | -90.0028 | -83.3267
1153 | 0.096083 | -3.1987 | 1.397 | 5.9973 | -0.0098904 | -9.196 | -26647.4912 | 3.1845 | -0.30102 | 49.4675 | 9.1552 | -0.86542 | 45.502 | -89.9835 | -83.3313
1154 | 0.096167 | -5.4156 | 1.3871 | 5.1295 | -0.010656 | -10.5451 | -26555.3128 | 5.3729 | -0.67876 | 49.4696 | 10.462 | -1.3217 | 45.5016 | -89.9642 | -83.3337
1155 | 0.09625 | -7.6238 | 1.3764 | 4.329 | -0.011464 | -11.9529 | -26437.0352 | 7.53 | -1.1926 | 49.4722 | 11.8057 | -1.8698 | 45.5015 | -89.9451 | -83.3339
1156 | 0.096333 | -9.8211 | 1.365 | 3.6015 | -0.012308 | -13.4226 | -26292.7747 | 9.6471 | -1.8403 | 49.4754 | 13.1848 | -2.5151 | 45.502 | -89.9261 | -83.332
1157 | 0.096417 | -12.0052 | 1.3527 | 2.9508 | -0.013179 | -14.956 | -26122.6735 | 11.7161 | -2.6189 | 49.479 | 14.5958 | -3.2626 | 45.5031 | -89.9073 | -83.328
1158 | 0.0965 | -14.1742 | 1.3395 | 2.379 | -0.014064 | -16.5532 | -25926.8991 | 13.7288 | -3.525 | 49.4832 | 16.0331 | -4.1166 | 45.5049 | -89.8887 | -83.322
1159 | 0.096583 | -16.3257 | 1.3254 | 1.886 | -0.014952 | -18.2117 | -25705.6445 | 15.6775 | -4.5547 | 49.4878 | 17.4886 | -5.0809 | 45.5075 | -89.8703 | -83.3142
1160 | 0.096667 | -18.4577 | 1.3105 | 1.4694 | -0.015827 | -19.9272 | -25459.1277 | 17.5543 | -5.7038 | 49.493 | 18.9518 | -6.1578 | 45.511 | -89.8521 | -83.3048
1161 | 0.09675 | -20.5682 | 1.2946 | 1.1248 | -0.016675 | -21.6929 | -25187.5918 | 19.3522 | -6.9672 | 49.4986 | 20.4105 | -7.3482 | 45.5153 | -89.8342 | -83.2939
1162 | 0.096833 | -22.655 | 1.278 | 0.84565 | -0.017487 | -23.5006 | -24891.3044 | 21.0641 | -8.3398 | 49.5047 | 21.8503 | -8.6512 | 45.5205 | -89.8166 | -83.2817
1163 | 0.096917 | -24.716 | 1.2605 | 0.62452 | -0.018254 | -25.3406 | -24570.5576 | 22.6833 | -9.8159 | 49.5113 | 23.2564 | -10.064 | 45.5265 | -89.7992 | -83.2686
1164 | 0.097 | -26.7494 | 1.2422 | 0.45308 | -0.01897 | -27.2025 | -24225.6678 | 24.2036 | -11.3893 | 49.5183 | 24.6135 | -11.5822 | 45.5334 | -89.7821 | -83.2548
1165 | 0.097083 | -28.753 | 1.2233 | 0.32295 | -0.019634 | -29.076 | -23856.975 | 25.6191 | -13.0536 | 49.5257 | 25.9069 | -13.2002 | 45.5411 | -89.7653 | -83.2404
1166 | 0.097167 | -30.7249 | 1.2036 | 0.22622 | -0.020247 | -30.9511 | -23464.8428 | 26.9244 | -14.8018 | 49.5336 | 27.1227 | -14.9108 | 45.5494 | -89.7489 | -83.2257
1167 | 0.09725 | -32.6632 | 1.1834 | 0.15576 | -0.02081 | -32.8189 | -23049.6579 | 28.1146 | -16.6269 | 49.5419 | 28.2486 | -16.7062 | 45.5584 | -89.7328 | -83.2109
1168 | 0.097333 | -34.5659 | 1.1626 | 0.10542 | -0.021328 | -34.6713 | -22611.8298 | 29.1849 | -18.5213 | 49.5507 | 29.274 | -18.5778 | 45.568 | -89.7171 | -83.1961
1169 | 0.097417 | -36.4312 | 1.1412 | 0.07015 | -0.021804 | -36.5013 | -22151.7902 | 30.1315 | -20.4774 | 49.5598 | 30.1895 | -20.5168 | 45.5781 | -89.7017 | -83.1814
1170 | 0.0975 | -38.2572 | 1.1194 | 0.04589 | -0.022242 | -38.3031 | -21669.993 | 30.9508 | -22.487 | 49.5693 | 30.9879 | -22.514 | 45.5887 | -89.6867 | -83.1671
1171 | 0.097583 | -40.0423 | 1.0972 | 0.02951 | -0.022644 | -40.0718 | -21166.9133 | 31.6396 | -24.5422 | 49.5792 | 31.6629 | -24.5603 | 45.5998 | -89.6721 | -83.153
1172 | 0.097667 | -41.7845 | 1.0745 | 0.018652 | -0.023014 | -41.8031 | -20643.0473 | 32.1955 | -26.6344 | 49.5895 | 32.2099 | -26.6463 | 45.6112 | -89.658 | -83.1394
1173 | 0.09775 | -43.4822 | 1.0515 | 0.011584 | -0.023354 | -43.4938 | -20098.9118 | 32.6165 | -28.7553 | 49.6001 | 32.6252 | -28.763 | 45.623 | -89.6442 | -83.1261
1174 | 0.097833 | -45.1338 | 1.0282 | 0.0070677 | -0.023664 | -45.1408 | -19535.0435 | 32.9011 | -30.8962 | 49.6111 | 32.9062 | -30.901 | 45.6351 | -89.6309 | -83.1134
1175 | 0.097917 | -46.7375 | 1.0045 | 0.0042345 | -0.023947 | -46.7417 | -18951.9985 | 33.0484 | -33.0484 | 49.6224 | 33.0514 | -33.0514 | 45.6476 | -89.618 | -83.1011
1176 | 0.098 | -48.2919 | 0.98057 | 0.0024904 | -0.024204 | -48.2944 | -18350.3521 | 33.0581 | -35.2033 | 49.634 | 33.0598 | -35.2051 | 45.6603 | -89.6056 | -83.0894
1177 | 0.098083 | -49.7954 | 0.95636 | 0.0014371 | -0.024433 | -49.7968 | -17730.6977 | 32.9303 | -37.3521 | 49.6459 | 32.9312 | -37.3532 | 45.6733 | -89.5936 | -83.0782
1178 | 0.098167 | -51.2465 | 0.93193 | 0.00081321 | -0.024637 | -51.2474 | -17093.6465 | 32.6658 | -39.4861 | 49.6581 | 32.6663 | -39.4868 | 45.6865 | -89.5822 | -83.0676
1179 | 0.09825 | -52.6439 | 0.90729 | 0.00045104 | -0.024815 | -52.6443 | -16439.827 | 32.2658 | -41.5968 | 49.6706 | 32.2661 | -41.5972 | 45.7 | -89.5712 | -83.0575
1180 | 0.098333 | -53.9861 | 0.88248 | 0.00024505 | -0.024966 | -53.9863 | -15769.8842 | 31.7322 | -43.6756 | 49.6833 | 31.7324 | -43.6758 | 45.7137 | -89.5606 | -83.0479
1181 | 0.098417 | -55.2718 | 0.85751 | 0.00013033 | -0.025092 | -55.2719 | -15084.4789 | 31.0673 | -45.7142 | 49.6963 | 31.0674 | -45.7143 | 45.7276 | -89.5506 | -83.039
1182 | 0.0985 | -56.4997 | 0.83242 | 6.7811e-05 | -0.025192 | -56.4998 | -14384.2874 | 30.2741 | -47.7043 | 49.7095 | 30.2741 | -47.7044 | 45.7417 | -89.5411 | -83.0306
1183 | 0.098583 | -57.6688 | 0.80723 | 3.4489e-05 | -0.025266 | -57.6688 | -13670.0002 | 29.3558 | -49.6379 | 49.723 | 29.3558 | -49.6379 | 45.7559 | -89.5321 | -83.0228
1184 | 0.098667 | -58.7777 | 0.78196 | 1.7133e-05 | -0.025314 | -58.7777 | -12942.3222 | 28.3164 | -51.5073 | 49.7366 | 28.3164 | -51.5073 | 45.7703 | -89.5237 | -83.0156
1185 | 0.09875 | -59.8255 | 0.75665 | 8.3066e-06 | -0.025336 | -59.8255 | -12201.9711 | 27.1602 | -53.3049 | 49.7505 | 27.1602 | -53.3049 | 45.7848 | -89.5157 | -83.0089
1186 | 0.098833 | -60.811 | 0.73131 | 3.9266e-06 | -0.025332 | -60.811 | -11449.6774 | 25.8921 | -55.0235 | 49.7645 | 25.8921 | -55.0235 | 45.7995 | -89.5083 | -83.0029
1187 | 0.098917 | -61.7334 | 0.70598 | 1.8079e-06 | -0.025302 | -61.7334 | -10686.1832 | 24.5173 | -56.6561 | 49.7787 | 24.5173 | -56.6561 | 45.8142 | -89.5014 | -82.9975
1188 | 0.099 | -62.5918 | 0.68068 | 8.0997e-07 | -0.025246 | -62.5918 | -9912.2417 | 23.0416 | -58.1963 | 49.793 | 23.0416 | -58.1963 | 45.8291 | -89.495 | -82.9926
1189 | 0.099083 | -63.3852 | 0.65543 | 3.5266e-07 | -0.025164 | -63.3852 | -9128.6165 | 21.471 | -59.6379 | 49.8074 | 21.471 | -59.6379 | 45.844 | -89.4892 | -82.9884
1190 | 0.099167 | -64.113 | 0.63027 | 1.4904e-07 | -0.025056 | -64.113 | -8336.0806 | 19.812 | -60.975 | 49.822 | 19.812 | -60.975 | 45.859 | -89.4839 | -82.9848
1191 | 0.09925 | -64.7743 | 0.60521 | 6.1053e-08 | -0.024923 | -64.7743 | -7535.4159 | 18.0715 | -62.2024 | 49.8366 | 18.0715 | -62.2024 | 45.874 | -89.4792 | -82.9817
1192 | 0.099333 | -65.3686 | 0.58029 | 2.4206e-08 | -0.024764 | -65.3686 | -6727.4123 | 16.2565 | -63.315 | 49.8514 | 16.2565 | -63.315 | 45.8891 | -89.475 | -82.9793
1193 | 0.099417 | -65.8954 | 0.55552 | 9.2731e-09 | -0.024579 | -65.8954 | -5912.8671 | 14.3746 | -64.3084 | 49.8662 | 14.3746 | -64.3084 | 45.9041 | -89.4714 | -82.9775
1194 | 0.0995 | -66.354 | 0.53094 | 3.4265e-09 | -0.024369 | -66.354 | -5092.5837 | 12.4335 | -65.1787 | 49.881 | 12.4335 | -65.1787 | 45.9192 | -89.4683 | -82.9762
1195 | 0.099583 | -66.744 | 0.50658 | 1.2188e-09 | -0.024135 | -66.744 | -4267.3714 | 10.4411 | -65.9223 | 49.8959 | 10.4411 | -65.9223 | 45.9343 | -89.4657 | -82.9756
1196 | 0.099667 | -67.0651 | 0.48244 | 4.1642e-10 | -0.023875 | -67.0651 | -3438.0444 | 8.4055 | -66.5363 | 49.9108 | 8.4055 | -66.5363 | 45.9493 | -89.4637 | -82.9755
1197 | 0.09975 | -67.3169 | 0.45857 | 1.3633e-10 | -0.023591 | -67.3169 | -2605.4209 | 6.3351 | -67.0182 | 49.9258 | 6.3351 | -67.0182 | 45.9643 | -89.4623 | -82.9761
1198 | 0.099833 | -67.4992 | 0.43498 | 4.2656e-11 | -0.023282 | -67.4992 | -1770.3223 | 4.2383 | -67.3661 | 49.9407 | 4.2383 | -67.3661 | 45.9792 | -89.4614 | -82.9772
1199 | 0.099917 | -67.6119 | 0.41169 | 1.2717e-11 | -0.02295 | -67.6119 | -933.5724 | 2.1237 | -67.5786 | 49.9556 | 2.1237 | -67.5786 | 45.994 | -89.461 | -82.9789
1200 | 0.1 | -67.6548 | 0.38874 | 3.6002e-12 | -0.022594 | -67.6548 | -95.9969 | 5.8014e-13 | -67.6548 | 49.9705 | 5.8014e-13 | -67.6548 | 46.0088 | -89.4612 | -82.9811
1201 | 0.10008 | -67.6279 | 0.36615 | 9.6433e-13 | -0.022215 | -67.6279 | 741.5779 | -2.1242 | -67.5945 | 49.9853 | -2.1242 | -67.5945 | 46.0234 | -89.4618 | -82.9839
1202 | 0.10017 | -67.5312 | 0.34393 | 2.4334e-13 | -0.021813 | -67.5312 | 1578.3257 | -4.2403 | -67.398 | 50 | -4.2403 | -67.398 | 46.038 | -89.4631 | -82.9873
1203 | 0.10025 | -67.3649 | 0.32212 | 5.7569e-14 | -0.021388 | -67.3649 | 2413.4211 | -6.3396 | -67.0659 | 50.0147 | -6.3396 | -67.0659 | 46.0524 | -89.4648 | -82.9913
1204 | 0.10033 | -67.1291 | 0.30073 | 1.2698e-14 | -0.020941 | -67.1291 | 3246.04 | -8.4135 | -66.5997 | 50.0293 | -8.4135 | -66.5997 | 46.0667 | -89.4671 | -82.9958
1205 | 0.10042 | -66.824 | 0.27979 | 2.595e-15 | -0.020473 | -66.824 | 4075.361 | -10.4536 | -66.0013 | 50.0438 | -10.4536 | -66.0013 | 46.0808 | -89.4699 | -83.0008
1206 | 0.1005 | -66.45 | 0.25932 | 4.8766e-16 | -0.019983 | -66.45 | 4900.5661 | -12.4515 | -65.273 | 50.0581 | -12.4515 | -65.273 | 46.0947 | -89.4732 | -83.0064
1207 | 0.10058 | -66.0074 | 0.23934 | 8.3544e-17 | -0.019473 | -66.0074 | 5720.8409 | -14.3991 | -64.4177 | 50.0723 | -14.3991 | -64.4177 | 46.1084 | -89.477 | -83.0125
1208 | 0.10067 | -65.4967 | 0.21986 | 1.2914e-17 | -0.018943 | -65.4967 | 6535.3763 | -16.2884 | -63.439 | 50.0864 | -16.2884 | -63.439 | 46.122 | -89.4812 | -83.019
1209 | 0.10075 | -64.9183 | 0.20092 | 1.7792e-18 | -0.018393 | -64.9183 | 7343.3687 | -18.1116 | -62.3407 | 50.1003 | -18.1116 | -62.3407 | 46.1354 | -89.486 | -83.0261
1210 | 0.10083 | -64.273 | 0.18253 | 2.1524e-19 | -0.017824 | -64.273 | 8144.0209 | -19.8614 | -61.1272 | 50.114 | -19.8614 | -61.1272 | 46.1485 | -89.4913 | -83.0337
1211 | 0.10092 | -63.5612 | 0.1647 | 2.2447e-20 | -0.017236 | -63.5612 | 8936.543 | -21.5306 | -59.8035 | 50.1276 | -21.5306 | -59.8035 | 46.1614 | -89.497 | -83.0418
1212 | 0.101 | -62.7838 | 0.14747 | 1.9724e-21 | -0.016631 | -62.7838 | 9720.1531 | -23.1123 | -58.3749 | 50.1409 | -23.1123 | -58.3749 | 46.174 | -89.5032 | -83.0504
1213 | 0.10108 | -61.9415 | 0.13084 | 1.4181e-22 | -0.016008 | -61.9415 | 10494.0781 | -24.5999 | -56.8471 | 50.1541 | -24.5999 | -56.8471 | 46.1864 | -89.5099 | -83.0594
1214 | 0.10117 | -61.0351 | 0.11483 | 8.0313e-24 | -0.015368 | -61.0351 | 11257.5545 | -25.9875 | -55.2262 | 50.167 | -25.9875 | -55.2262 | 46.1986 | -89.517 | -83.0688
1215 | 0.10125 | -60.0655 | 0.09946 | 3.404e-25 | -0.014712 | -60.0655 | 12009.8292 | -27.2692 | -53.5188 | 50.1797 | -27.2692 | -53.5188 | 46.2104 | -89.5245 | -83.0787
1216 | 0.10133 | -59.0338 | 0.084747 | 1.0058e-26 | -0.014041 | -59.0338 | 12750.1598 | -28.4397 | -51.7317 | 50.1921 | -28.4397 | -51.7317 | 46.222 | -89.5324 | -83.089
1217 | 0.10142 | -57.9408 | 0.070706 | 1.8699e-28 | -0.013355 | -57.9408 | 13477.8161 | -29.4943 | -49.8721 | 50.2043 | -29.4943 | -49.8721 | 46.2333 | -89.5408 | -83.0998
1218 | 0.1015 | -56.7878 | 0.057351 | 1.8693e-30 | -0.012655 | -56.7878 | 14192.0802 | -30.4284 | -47.9475 | 50.2162 | -30.4284 | -47.9475 | 46.2443 | -89.5496 | -83.1109
1219 | 0.10158 | -55.5759 | 0.044696 | 7.7568e-33 | -0.011941 | -55.5759 | 14892.2475 | -31.2383 | -45.9657 | 50.2278 | -31.2383 | -45.9657 | 46.2549 | -89.5588 | -83.1224
1220 | 0.10167 | -54.3062 | 0.032755 | 8.3127e-36 | -0.011215 | -54.3062 | 15577.6271 | -31.9204 | -43.9346 | 50.2392 | -31.9204 | -43.9346 | 46.2653 | -89.5683 | -83.1343
1221 | 0.10175 | -52.98 | 0.021539 | 8.2199e-40 | -0.010477 | -52.98 | 16247.5429 | -32.4718 | -41.8624 | 50.2503 | -32.4718 | -41.8624 | 46.2753 | -89.5783 | -83.1465
1222 | 0.10183 | -51.5987 | 0.011062 | 3.5348e-46 | -0.0097275 | -51.5987 | 16901.3341 | -32.8903 | -39.7575 | 50.261 | -32.8903 | -39.7575 | 46.2849 | -89.5885 | -83.1591
1223 | 0.10192 | -50.1636 | 0.0013348 | 2.201e-66 | -0.0089675 | -50.1636 | 17538.3556 | -33.1738 | -37.6283 | 50.2714 | -33.1738 | -37.6283 | 46.2943 | -89.5992 | -83.1721
1224 | 0.102 | -48.6761 | -0.0076328 | -1.0065e-49 | -0.0081978 | -48.6761 | 18157.9791 | -33.3211 | -35.4834 | 50.2815 | -33.3211 | -35.4834 | 46.3032 | -89.6102 | -83.1853
1225 | 0.10208 | -47.1378 | -0.015831 | -9.3906e-43 | -0.007419 | -47.1378 | 18759.5933 | -33.3314 | -33.3314 | 50.2913 | -33.3314 | -33.3314 | 46.3119 | -89.6215 | -83.1988
1226 | 0.10217 | -45.5501 | -0.02325 | -4.4148e-39 | -0.006632 | -45.5501 | 19342.6046 | -33.2046 | -31.1812 | 50.3008 | -33.2046 | -31.1812 | 46.3201 | -89.6331 | -83.2127
1227 | 0.10225 | -43.9146 | -0.029882 | -1.1032e-36 | -0.0058376 | -43.9146 | 19906.4381 | -32.9408 | -29.0412 | 50.3099 | -32.9408 | -29.0412 | 46.328 | -89.645 | -83.2268
1228 | 0.10233 | -42.2329 | -0.035719 | -5.5927e-35 | -0.0050365 | -42.2329 | 20450.5374 | -32.541 | -26.9202 | 50.3186 | -32.541 | -26.9202 | 46.3355 | -89.6571 | -83.2411
1229 | 0.10242 | -40.5067 | -0.040756 | -1.0184e-33 | -0.0042295 | -40.5067 | 20974.3658 | -32.0066 | -24.8268 | 50.327 | -32.0066 | -24.8268 | 46.3426 | -89.6696 | -83.2557
1230 | 0.1025 | -38.7377 | -0.044985 | -8.9395e-33 | -0.0034175 | -38.7377 | 21477.4066 | -31.3395 | -22.7695 | 50.335 | -31.3395 | -22.7695 | 46.3493 | -89.6823 | -83.2706
1231 | 0.10258 | -36.9277 | -0.048403 | -4.4762e-32 | -0.0026012 | -36.9277 | 21959.1637 | -30.5422 | -20.7565 | 50.3427 | -30.5422 | -20.7565 | 46.3556 | -89.6953 | -83.2856
1232 | 0.10267 | -35.0785 | -0.051004 | -1.4159e-31 | -0.0017814 | -35.0785 | 22419.1617 | -29.6177 | -18.796 | 50.3499 | -29.6177 | -18.796 | 46.3615 | -89.7084 | -83.3008
1233 | 0.10275 | -33.1918 | -0.052785 | -3.0133e-31 | -0.00095895 | -33.1918 | 22856.947 | -28.5696 | -16.896 | 50.3568 | -28.5696 | -16.896 | 46.3671 | -89.7218 | -83.3162
1234 | 0.10283 | -31.2696 | -0.053744 | -4.4778e-31 | -0.00013468 | -31.2696 | 23272.0878 | -27.4018 | -15.0642 | 50.3633 | -27.4018 | -15.0642 | 46.3722 | -89.7354 | -83.3318
1235 | 0.10292 | -29.3138 | -0.053879 | -4.7313e-31 | 0.00069061 | -29.3138 | 23664.1745 | -26.1188 | -13.3082 | 50.3694 | -26.1188 | -13.3082 | 46.3769 | -89.7492 | -83.3475
1236 | 0.103 | -27.3262 | -0.053188 | -3.5622e-31 | 0.0015161 | -27.3262 | 24032.8206 | -24.7255 | -11.6349 | 50.3751 | -24.7255 | -11.6349 | 46.3812 | -89.7632 | -83.3634
1237 | 0.10308 | -25.309 | -0.051672 | -1.8855e-31 | 0.002341 | -25.309 | 24377.6623 | -23.2274 | -10.0514 | 50.3804 | -23.2274 | -10.0514 | 46.3851 | -89.7773 | -83.3793
1238 | 0.10317 | -23.264 | -0.049331 | -6.799e-32 | 0.0031644 | -23.264 | 24698.3596 | -21.6303 | -8.564 | 50.3853 | -21.6303 | -8.564 | 46.3886 | -89.7915 | -83.3954
1239 | 0.10325 | -21.1932 | -0.046167 | -1.5813e-32 | 0.0039856 | -21.1932 | 24994.5963 | -19.9403 | -7.179 | 50.3898 | -19.9403 | -7.179 | 46.3917 | -89.8059 | -83.4115
1240 | 0.10333 | -19.0989 | -0.042181 | -2.1696e-33 | 0.0048038 | -19.0989 | 25266.0801 | -18.1641 | -5.9019 | 50.3939 | -18.1641 | -5.9019 | 46.3943 | -89.8204 | -83.4277
1241 | 0.10342 | -16.9829 | -0.037377 | -1.5176e-34 | 0.005618 | -16.9829 | 25512.5435 | -16.3086 | -4.7381 | 50.3976 | -16.3086 | -4.7381 | 46.3965 | -89.835 | -83.444
1242 | 0.1035 | -14.8475 | -0.031759 | -4.2165e-36 | 0.0064277 | -14.8475 | 25733.7434 | -14.381 | -3.6924 | 50.4009 | -14.381 | -3.6924 | 46.3984 | -89.8497 | -83.4603
1243 | 0.10358 | -12.6947 | -0.025332 | -2.9133e-38 | 0.0072318 | -12.6947 | 25929.4618 | -12.3889 | -2.7693 | 50.4038 | -12.3889 | -2.7693 | 46.3998 | -89.8644 | -83.4766
1244 | 0.10367 | -10.5266 | -0.0181 | -1.7892e-41 | 0.0080296 | -10.5266 | 26099.5056 | -10.3402 | -1.9725 | 50.4062 | -10.3402 | -1.9725 | 46.4008 | -89.8792 | -83.4929
1245 | 0.10375 | -8.3455 | -0.01007 | -4.4741e-47 | 0.0088204 | -8.3455 | 26243.7074 | -8.2427 | -1.3055 | 50.4082 | -8.2427 | -1.3055 | 46.4013 | -89.8941 | -83.5092
1246 | 0.10383 | -6.1534 | -0.0012499 | -5.1857e-67 | 0.0096034 | -6.1534 | 26361.925 | -6.1049 | -0.77122 | 50.4099 | -6.1049 | -0.77122 | 46.4015 | -89.9089 | -83.5255
1247 | 0.10392 | -3.9525 | 0.0083535 | 7.3265e-49 | 0.010378 | -3.9525 | 26454.042 | -3.935 | -0.37197 | 50.4111 | -3.935 | -0.37197 | 46.4012 | -89.9238 | -83.5417
1248 | 0.104 | -1.7451 | 0.018731 | 3.804e-41 | 0.011143 | -1.7451 | 26519.9677 | -1.7417 | -0.10958 | 50.4119 | -1.7417 | -0.10958 | 46.4006 | -89.9387 | -83.5579
1249 | 0.10408 | 0.46672 | 0.029874 | 1.097e-36 | 0.011898 | 0.46672 | 26559.6373 | 0.46649 | 0.01466 | 50.4123 | 0.46649 | 0.01466 | 46.3995 | -89.9535 | -83.574
1250 | 0.10417 | 2.6808 | 0.041771 | 1.7503e-33 | 0.012641 | 2.6808 | 26573.0118 | 2.6808 | 1.839e-14 | 50.4123 | 2.6808 | 1.839e-14 | 46.3981 | -89.9684 | -83.59
1251 | 0.10425 | 4.8948 | 0.054413 | 5.8777e-31 | 0.013374 | 4.8948 | 26560.0783 | 4.8924 | -0.15375 | 50.4119 | 4.8924 | -0.15375 | 46.3962 | -89.9831 | -83.6059
1252 | 0.10433 | 7.1067 | 0.067787 | 7.3949e-29 | 0.014094 | 7.1067 | 26520.8497 | 7.0927 | -0.44623 | 50.4111 | 7.0927 | -0.44623 | 46.394 | -89.9979 | -83.6217
1253 | 0.10442 | 9.3142 | 0.08188 | 4.7175e-27 | 0.014801 | 9.3142 | 26455.3649 | 9.2729 | -0.87655 | 50.4098 | 9.2729 | -0.87655 | 46.3913 | -90.0125 | -83.6373
1254 | 0.1045 | 11.5152 | 0.096681 | 1.825e-25 | 0.015494 | 11.5152 | 26363.6889 | 11.4244 | -1.4432 | 50.4082 | 11.4244 | -1.4432 | 46.3883 | -90.0271 | -83.6528
1255 | 0.10458 | 13.7075 | 0.11217 | 4.8023e-24 | 0.016172 | 13.7075 | 26245.9123 | 13.5387 | -2.1443 | 50.4062 | 13.5387 | -2.1443 | 46.3849 | -90.0415 | -83.6681
1256 | 0.10467 | 15.8888 | 0.12835 | 9.295e-23 | 0.016836 | 15.8888 | 26102.1515 | 15.6074 | -2.9773 | 50.4038 | 15.6074 | -2.9773 | 46.3811 | -90.0558 | -83.6833
1257 | 0.10475 | 18.0571 | 0.14518 | 1.3993e-21 | 0.017484 | 18.0571 | 25932.5487 | 17.6222 | -3.939 | 50.4011 | 17.6222 | -3.939 | 46.377 | -90.0701 | -83.6983
1258 | 0.10483 | 20.2102 | 0.16267 | 1.7074e-20 | 0.018115 | 20.2102 | 25737.2714 | 19.5752 | -5.0261 | 50.3979 | 19.5752 | -5.0261 | 46.3725 | -90.0841 | -83.713
1259 | 0.10492 | 22.3459 | 0.18078 | 1.7425e-19 | 0.018729 | 22.3459 | 25516.5126 | 21.4587 | -6.2343 | 50.3944 | 21.4587 | -6.2343 | 46.3676 | -90.098 | -83.7276
1260 | 0.105 | 24.4622 | 0.19951 | 1.5242e-18 | 0.019326 | 24.4622 | 25270.4903 | 23.265 | -7.5592 | 50.3905 | 23.265 | -7.5592 | 46.3624 | -90.1118 | -83.7419
1261 | 0.10508 | 26.557 | 0.21884 | 1.1653e-17 | 0.019905 | 26.557 | 24999.4476 | 24.987 | -8.9959 | 50.3862 | 24.987 | -8.9959 | 46.3568 | -90.1254 | -83.756
1262 | 0.10517 | 28.6281 | 0.23874 | 7.9102e-17 | 0.020464 | 28.6281 | 24703.6521 | 26.6178 | -10.5387 | 50.3816 | 26.6178 | -10.5387 | 46.3509 | -90.1387 | -83.7698
1263 | 0.10525 | 30.6736 | 0.25921 | 4.8301e-16 | 0.021004 | 30.6736 | 24383.396 | 28.1508 | -12.182 | 50.3766 | 28.1508 | -12.182 | 46.3447 | -90.1519 | -83.7833
1264 | 0.10533 | 32.6914 | 0.28021 | 2.6817e-15 | 0.021525 | 32.6914 | 24038.9955 | 29.58 | -13.9193 | 50.3713 | 29.58 | -13.9193 | 46.3381 | -90.1649 | -83.7966
1265 | 0.10542 | 34.6794 | 0.30174 | 1.3662e-14 | 0.022025 | 34.6794 | 23670.7908 | 30.8996 | -15.7441 | 50.3656 | 30.8996 | -15.7441 | 46.3312 | -90.1776 | -83.8096
1266 | 0.1055 | 36.6358 | 0.32376 | 6.4367e-14 | 0.022504 | 36.6358 | 23279.1453 | 32.1042 | -17.6494 | 50.3596 | 32.1042 | -17.6494 | 46.3241 | -90.1901 | -83.8222
1267 | 0.10558 | 38.5586 | 0.34626 | 2.8229e-13 | 0.022961 | 38.5586 | 22864.446 | 33.189 | -19.6279 | 50.3533 | 33.189 | -19.6279 | 46.3166 | -90.2023 | -83.8346
1268 | 0.10567 | 40.4459 | 0.36922 | 1.1592e-12 | 0.023397 | 40.4459 | 22427.1021 | 34.1496 | -21.672 | 50.3467 | 34.1496 | -21.672 | 46.3089 | -90.2143 | -83.8466
1269 | 0.10575 | 42.2959 | 0.39262 | 4.4791e-12 | 0.02381 | 42.2959 | 21967.5455 | 34.9821 | -23.7738 | 50.3397 | 34.9821 | -23.7738 | 46.3008 | -90.226 | -83.8584
1270 | 0.10583 | 44.1066 | 0.41643 | 1.6358e-11 | 0.024201 | 44.1066 | 21486.23 | 35.683 | -25.9252 | 50.3325 | 35.683 | -25.9252 | 46.2925 | -90.2375 | -83.8697
1271 | 0.10592 | 45.8763 | 0.44063 | 5.6683e-11 | 0.024569 | 45.8763 | 20983.6308 | 36.2494 | -28.1179 | 50.325 | 36.2494 | -28.1179 | 46.2839 | -90.2486 | -83.8807
1272 | 0.106 | 47.6033 | 0.4652 | 1.8701e-10 | 0.024913 | 47.6033 | 20460.244 | 36.679 | -30.3435 | 50.3172 | 36.679 | -30.3435 | 46.2751 | -90.2594 | -83.8914
1273 | 0.10608 | 49.2858 | 0.49012 | 5.8928e-10 | 0.025234 | 49.2858 | 19916.5865 | 36.9698 | -32.5933 | 50.3091 | 36.9698 | -32.5933 | 46.2661 | -90.27 | -83.9016
1274 | 0.10617 | 50.9222 | 0.51535 | 1.7782e-09 | 0.02553 | 50.9222 | 19353.1948 | 37.1207 | -34.8586 | 50.3007 | 37.1207 | -34.8586 | 46.2568 | -90.2802 | -83.9115
1275 | 0.10625 | 52.5108 | 0.54088 | 5.1518e-09 | 0.025802 | 52.5108 | 18770.6254 | 37.1307 | -37.1307 | 50.2921 | 37.1307 | -37.1307 | 46.2473 | -90.2901 | -83.921
1276 | 0.10633 | 54.0501 | 0.56668 | 1.4362e-08 | 0.026049 | 54.0501 | 18169.4531 | 36.9998 | -39.4008 | 50.2833 | 36.9998 | -39.4008 | 46.2376 | -90.2996 | -83.9301
1277 | 0.10642 | 55.5385 | 0.59273 | 3.8603e-08 | 0.026272 | 55.5385 | 17550.2717 | 36.7283 | -41.6601 | 50.2742 | 36.7283 | -41.6601 | 46.2277 | -90.3089 | -83.9389
1278 | 0.1065 | 56.9747 | 0.619 | 1.0023e-07 | 0.026469 | 56.9747 | 16913.6922 | 36.317 | -43.8997 | 50.2649 | 36.317 | -43.8997 | 46.2176 | -90.3177 | -83.9472
1279 | 0.10658 | 58.357 | 0.64547 | 2.518e-07 | 0.026641 | 58.357 | 16260.3433 | 35.7674 | -46.1111 | 50.2554 | 35.7674 | -46.1111 | 46.2073 | -90.3262 | -83.955
1280 | 0.10667 | 59.6843 | 0.67211 | 6.1302e-07 | 0.026787 | 59.6843 | 15590.8697 | 35.0815 | -48.2856 | 50.2457 | 35.0815 | -48.2856 | 46.1968 | -90.3344 | -83.9625
1281 | 0.10675 | 60.9551 | 0.6989 | 1.4484e-06 | 0.026908 | 60.9551 | 14905.9325 | 34.2618 | -50.4148 | 50.2358 | 34.2618 | -50.4148 | 46.1862 | -90.3421 | -83.9696
1282 | 0.10683 | 62.1682 | 0.72581 | 3.3253e-06 | 0.027003 | 62.1682 | 14206.2077 | 33.3114 | -52.4903 | 50.2257 | 33.3114 | -52.4903 | 46.1755 | -90.3495 | -83.9762
1283 | 0.10692 | 63.3224 | 0.75281 | 7.4276e-06 | 0.027072 | 63.3224 | 13492.3862 | 32.2337 | -54.5042 | 50.2155 | 32.2337 | -54.5042 | 46.1646 | -90.3566 | -83.9823
1284 | 0.107 | 64.4165 | 0.77988 | 1.6159e-05 | 0.027116 | 64.4165 | 12765.1726 | 31.0329 | -56.4486 | 50.205 | 31.0329 | -56.4486 | 46.1536 | -90.3632 | -83.9881
1285 | 0.10708 | 65.4496 | 0.807 | 3.4274e-05 | 0.027133 | 65.4495 | 12025.2847 | 29.7135 | -58.316 | 50.1945 | 29.7135 | -58.316 | 46.1425 | -90.3694 | -83.9934
1286 | 0.10717 | 66.4204 | 0.83413 | 7.0945e-05 | 0.027124 | 66.4204 | 11273.4529 | 28.2804 | -60.099 | 50.1838 | 28.2804 | -60.0989 | 46.1313 | -90.3753 | -83.9982
1287 | 0.10725 | 67.3282 | 0.86126 | 0.00014344 | 0.027089 | 67.328 | 10510.4194 | 26.7392 | -61.7907 | 50.1729 | 26.7392 | -61.7906 | 46.12 | -90.3807 | -84.0026
1288 | 0.10733 | 68.1719 | 0.88834 | 0.0002835 | 0.027028 | 68.1716 | 9736.9375 | 25.0957 | -63.3846 | 50.162 | 25.0956 | -63.3843 | 46.1087 | -90.3858 | -84.0065
1289 | 0.10742 | 68.9507 | 0.91537 | 0.00054816 | 0.02694 | 68.9502 | 8953.7706 | 23.3562 | -64.8744 | 50.1509 | 23.356 | -64.8739 | 46.0973 | -90.3904 | -84.01
1290 | 0.1075 | 69.6639 | 0.94231 | 0.0010376 | 0.026826 | 69.6629 | 8161.6918 | 21.5273 | -66.2543 | 50.1398 | 21.527 | -66.2533 | 46.0859 | -90.3947 | -84.013
1291 | 0.10758 | 70.3108 | 0.96914 | 0.0019241 | 0.026685 | 70.3088 | 7361.4831 | 19.6161 | -67.519 | 50.1285 | 19.6155 | -67.5171 | 46.0745 | -90.3985 | -84.0156
1292 | 0.10767 | 70.8906 | 0.99582 | 0.0034975 | 0.026516 | 70.8871 | 6553.9343 | 17.6298 | -68.6635 | 50.1172 | 17.6289 | -68.6601 | 46.0633 | -90.4019 | -84.0176
1293 | 0.10775 | 71.4029 | 1.0223 | 0.006235 | 0.026318 | 71.3967 | 5739.8426 | 15.5761 | -69.6833 | 50.1059 | 15.5747 | -69.6772 | 46.0522 | -90.4049 | -84.0192
1294 | 0.10783 | 71.8471 | 1.0487 | 0.010906 | 0.026089 | 71.8362 | 4920.0116 | 13.4628 | -70.5745 | 50.0945 | 13.4608 | -70.5638 | 46.0414 | -90.4075 | -84.0204
1295 | 0.10792 | 72.2228 | 1.0747 | 0.018727 | 0.025826 | 72.204 | 4095.2505 | 11.2981 | -71.3336 | 50.0831 | 11.2952 | -71.3151 | 46.0312 | -90.4097 | -84.021
1296 | 0.108 | 72.5295 | 1.1006 | 0.031576 | 0.025525 | 72.498 | 3266.3736 | 9.0904 | -71.9576 | 50.0716 | 9.0864 | -71.9263 | 46.0218 | -90.4114 | -84.0213
1297 | 0.10808 | 72.7671 | 1.1261 | 0.052289 | 0.025178 | 72.7148 | 2434.1989 | 6.848 | -72.4441 | 50.0601 | 6.8431 | -72.3921 | 46.0136 | -90.4127 | -84.0212
1298 | 0.10817 | 72.9352 | 1.1513 | 0.085051 | 0.024777 | 72.8501 | 1599.5479 | 4.5796 | -72.7912 | 50.0486 | 4.5743 | -72.7064 | 46.0071 | -90.4137 | -84.0209
1299 | 0.10825 | 73.0336 | 1.176 | 0.13587 | 0.024309 | 72.8978 | 763.2446 | 2.294 | -72.9976 | 50.0372 | 2.2898 | -72.8618 | 46.0032 | -90.4142 | -84.0205
1300 | 0.10833 | 73.0623 | 1.2004 | 0.21311 | 0.023758 | 72.8492 | -73.8855 | 3.7589e-13 | -73.0623 | 50.0257 | 3.7479e-13 | -72.8492 | 46.0026 | -90.4143 | -84.0204
1301 | 0.10842 | 73.0213 | 1.2241 | 0.32799 | 0.023106 | 72.6933 | -911.0162 | -2.2937 | -72.9853 | 50.0143 | -2.2834 | -72.6574 | 46.0063 | -90.414 | -84.021
1302 | 0.1085 | 72.9105 | 1.2472 | 0.49491 | 0.022332 | 72.4156 | -1747.321 | -4.5781 | -72.7667 | 50.003 | -4.547 | -72.2727 | 46.0152 | -90.4132 | -84.0229
1303 | 0.10858 | 72.7301 | 1.2696 | 0.73129 | 0.021418 | 71.9988 | -2581.9745 | -6.8445 | -72.4074 | 49.9916 | -6.7757 | -71.6793 | 46.0303 | -90.4121 | -84.0267
1304 | 0.10867 | 72.4803 | 1.291 | 1.0567 | 0.020354 | 71.4236 | -3414.1527 | -9.0842 | -71.9087 | 49.9804 | -8.9518 | -70.8604 | 46.052 | -90.4106 | -84.033
1305 | 0.10875 | 72.1612 | 1.3113 | 1.4907 | 0.019141 | 70.6705 | -4243.0343 | -11.2885 | -71.2728 | 49.9692 | -11.0553 | -69.8004 | 46.0805 | -90.4086 | -84.0425
1306 | 0.10883 | 71.7732 | 1.3305 | 2.0505 | 0.017799 | 69.7227 | -5067.8009 | -13.449 | -70.5019 | 49.9582 | -13.0647 | -68.4878 | 46.1158 | -90.4063 | -84.0557
1307 | 0.10892 | 71.3167 | 1.3483 | 2.7468 | 0.016363 | 68.5699 | -5887.6385 | -15.5573 | -69.5992 | 49.9472 | -14.9581 | -66.9185 | 46.1572 | -90.4036 | -84.0729
1308 | 0.109 | 70.7921 | 1.3646 | 3.5817 | 0.014882 | 67.2104 | -6701.7378 | -17.6053 | -68.568 | 49.9363 | -16.7146 | -65.0989 | 46.2038 | -90.4005 | -84.0944
1309 | 0.10908 | 70.1999 | 1.3795 | 4.5469 | 0.013407 | 65.653 | -7509.2952 | -19.5852 | -67.4125 | 49.9255 | -18.3166 | -63.0462 | 46.2548 | -90.397 | -84.12
1310 | 0.10917 | 69.5408 | 1.3929 | 5.625 | 0.011983 | 63.9157 | -8309.5136 | -21.4893 | -66.1372 | 49.9149 | -19.751 | -60.7875 | 46.309 | -90.3931 | -84.1497
1311 | 0.10925 | 68.8152 | 1.4049 | 6.7916 | 0.010645 | 62.0236 | -9101.6029 | -23.3103 | -64.7469 | 49.9044 | -21.0098 | -58.3568 | 46.3654 | -90.3889 | -84.1832
1312 | 0.10933 | 68.0241 | 1.4155 | 8.0185 | 0.0094103 | 60.0056 | -9884.7815 | -25.0413 | -63.2472 | 49.8941 | -22.0895 | -55.7918 | 46.4231 | -90.3843 | -84.2201
1313 | 0.10942 | 67.168 | 1.425 | 9.2768 | 0.0082878 | 57.8912 | -10658.2761 | -26.6756 | -61.6438 | 49.8839 | -22.9914 | -53.1299 | 46.4811 | -90.3793 | -84.26
1314 | 0.1095 | 66.248 | 1.4332 | 10.5392 | 0.0072758 | 55.7088 | -11421.3232 | -28.207 | -59.943 | 49.8739 | -23.7196 | -50.4068 | 46.5387 | -90.374 | -84.3025
1315 | 0.10958 | 65.2648 | 1.4405 | 11.7812 | 0.0063678 | 53.4836 | -12173.1697 | -29.6296 | -58.1514 | 49.8641 | -24.2811 | -47.6542 | 46.5954 | -90.3683 | -84.3472
1316 | 0.10967 | 64.2195 | 1.4469 | 12.9817 | 0.0055542 | 51.2377 | -12913.0733 | -30.938 | -56.2759 | 49.8544 | -24.684 | -44.9 | 46.6506 | -90.3623 | -84.3938
1317 | 0.10975 | 63.113 | 1.4524 | 14.1234 | 0.0048243 | 48.9896 | -13640.3036 | -32.1271 | -54.324 | 49.845 | -24.9377 | -42.1674 | 46.7041 | -90.356 | -84.4418
1318 | 0.10983 | 61.9464 | 1.4573 | 15.1922 | 0.0041677 | 46.7542 | -14354.1429 | -33.1926 | -52.3031 | 49.8357 | -25.0522 | -39.4759 | 46.7555 | -90.3493 | -84.4909
1319 | 0.10992 | 60.721 | 1.4614 | 16.1774 | 0.0035745 | 44.5436 | -15053.8864 | -34.1303 | -50.2212 | 49.8267 | -25.0372 | -36.8412 | 46.8045 | -90.3423 | -84.5407
1320 | 0.11 | 59.4379 | 1.465 | 17.0706 | 0.0030358 | 42.3673 | -15738.8434 | -34.9367 | -48.0862 | 49.8178 | -24.9029 | -34.2759 | 46.8511 | -90.3351 | -84.5911
1321 | 0.11008 | 58.0983 | 1.468 | 17.866 | 0.0025437 | 40.2323 | -16408.3377 | -35.6089 | -45.9067 | 49.8093 | -24.6587 | -31.7898 | 46.8952 | -90.3275 | -84.6416
1322 | 0.11017 | 56.7036 | 1.4706 | 18.5595 | 0.0020913 | 38.1441 | -17061.7085 | -36.1442 | -43.6909 | 49.8009 | -24.3139 | -29.3905 | 46.9367 | -90.3196 | -84.6921
1323 | 0.11025 | 55.2551 | 1.4727 | 19.1489 | 0.0016726 | 36.1062 | -17698.3107 | -36.5409 | -41.4475 | 49.7928 | -23.8775 | -27.0837 | 46.9755 | -90.3115 | -84.7424
1324 | 0.11033 | 53.7544 | 1.4744 | 19.6332 | 0.0012824 | 34.1212 | -18317.516 | -36.7974 | -39.1852 | 49.7849 | -23.3576 | -24.8733 | 47.0118 | -90.303 | -84.7923
1325 | 0.11042 | 52.2027 | 1.4756 | 20.0123 | 0.00091613 | 32.1904 | -18918.713 | -36.9129 | -36.9129 | 49.7773 | -22.762 | -22.762 | 47.0455 | -90.2944 | -84.8415
1326 | 0.1105 | 50.6018 | 1.4766 | 20.2875 | 0.00056971 | 30.3143 | -19501.3084 | -36.8871 | -34.6393 | 49.7699 | -22.0982 | -20.7516 | 47.0767 | -90.2854 | -84.89
1327 | 0.11058 | 48.953 | 1.4771 | 20.4604 | 0.00023962 | 28.4927 | -20064.7268 | -36.7202 | -32.3732 | 49.7628 | -21.3727 | -18.8425 | 47.1054 | -90.2763 | -84.9376
1328 | 0.11067 | 47.2582 | 1.4774 | 20.5335 | -7.7299e-05 | 26.7247 | -20608.4123 | -36.4131 | -30.1235 | 49.756 | -20.5917 | -17.035 | 47.1318 | -90.2669 | -84.9842
1329 | 0.11075 | 45.5189 | 1.4773 | 20.5099 | -0.00038391 | 25.009 | -21131.8279 | -35.967 | -27.8988 | 49.7495 | -19.761 | -15.3282 | 47.1559 | -90.2573 | -85.0296
1330 | 0.11083 | 43.7368 | 1.4769 | 20.3929 | -0.00068282 | 23.3439 | -21634.4571 | -35.3838 | -25.7078 | 49.7432 | -18.8856 | -13.7212 | 47.1779 | -90.2474 | -85.0739
1331 | 0.11092 | 41.9137 | 1.4762 | 20.1865 | -0.00097648 | 21.7272 | -22115.8035 | -34.666 | -23.559 | 49.7372 | -17.9701 | -12.2125 | 47.1977 | -90.2374 | -85.1168
1332 | 0.111 | 40.0514 | 1.4752 | 19.8948 | -0.0012672 | 20.1566 | -22575.392 | -33.8165 | -21.4606 | 49.7316 | -17.0188 | -10.8005 | 47.2155 | -90.2272 | -85.1584
1333 | 0.11108 | 38.1518 | 1.474 | 19.5222 | -0.0015571 | 18.6296 | -23012.7688 | -32.8388 | -19.4208 | 49.7262 | -16.0352 | -9.4832 | 47.2315 | -90.2168 | -85.1985
1334 | 0.11117 | 36.2166 | 1.4724 | 19.0735 | -0.0018484 | 17.1431 | -23427.5022 | -31.7368 | -17.4475 | 49.7211 | -15.0226 | -8.2587 | 47.2457 | -90.2063 | -85.2371
1335 | 0.11125 | 34.2478 | 1.4706 | 18.5536 | -0.0021431 | 15.6942 | -23819.1826 | -30.515 | -15.5482 | 49.7163 | -13.9836 | -7.125 | 47.2582 | -90.1956 | -85.2742
1336 | 0.11133 | 32.2474 | 1.4684 | 17.9678 | -0.0024436 | 14.2796 | -24187.4233 | -29.1783 | -13.7303 | 49.7119 | -12.9206 | -6.08 | 47.2692 | -90.1847 | -85.3098
1337 | 0.11142 | 30.2172 | 1.466 | 17.3214 | -0.0027519 | 12.8959 | -24531.8608 | -27.732 | -12.0007 | 49.7077 | -11.8353 | -5.1216 | 47.2787 | -90.1737 | -85.3437
1338 | 0.1115 | 28.1594 | 1.4632 | 16.62 | -0.0030703 | 11.5395 | -24852.155 | -26.182 | -10.3662 | 49.7039 | -10.7291 | -4.248 | 47.2868 | -90.1627 | -85.376
1339 | 0.11158 | 26.0759 | 1.4602 | 15.8694 | -0.0034013 | 10.2065 | -25147.9895 | -24.5343 | -8.8329 | 49.7004 | -9.6031 | -3.4573 | 47.2937 | -90.1515 | -85.4066
1340 | 0.11167 | 23.9688 | 1.4568 | 15.0757 | -0.0037472 | 8.893 | -25419.0724 | -22.7957 | -7.4068 | 49.6971 | -8.4578 | -2.7481 | 47.2994 | -90.1402 | -85.4355
1341 | 0.11175 | 21.8401 | 1.453 | 14.2452 | -0.0041109 | 7.5949 | -25665.1357 | -20.9729 | -6.0932 | 49.6943 | -7.2933 | -2.1189 | 47.304 | -90.1288 | -85.4626
1342 | 0.11183 | 19.6919 | 1.4489 | 13.3844 | -0.0044951 | 6.3075 | -25885.9367 | -19.0733 | -4.8972 | 49.6917 | -6.1094 | -1.5686 | 47.3076 | -90.1174 | -85.488
1343 | 0.11192 | 17.5265 | 1.4444 | 12.5 | -0.0049028 | 5.0264 | -26081.2571 | -17.1044 | -3.8233 | 49.6894 | -4.9054 | -1.0965 | 47.3104 | -90.1059 | -85.5117
1344 | 0.112 | 15.3458 | 1.4395 | 11.5991 | -0.0053372 | 3.7467 | -26250.9041 | -15.074 | -2.8755 | 49.6875 | -3.6803 | -0.70206 | 47.3124 | -90.0943 | -85.5336
1345 | 0.11208 | 13.152 | 1.4342 | 10.6889 | -0.0058015 | 2.4631 | -26394.71 | -12.9901 | -2.0574 | 49.6859 | -2.4328 | -0.38532 | 47.3137 | -90.0827 | -85.5536
1346 | 0.11217 | 10.9474 | 1.4284 | 9.777 | -0.0062989 | 1.1704 | -26512.5328 | -10.8611 | -1.3721 | 49.6846 | -1.1612 | -0.14669 | 47.3144 | -90.0711 | -85.5718
1347 | 0.11225 | 8.734 | 1.4221 | 8.8711 | -0.0068326 | -0.13712 | -26604.2561 | -8.6952 | -0.82194 | 49.6837 | 0.13651 | 0.012904 | 47.3147 | -90.0595 | -85.5881
1348 | 0.11233 | 6.5141 | 1.4152 | 7.9792 | -0.0074057 | -1.4652 | -26669.789 | -6.5012 | -0.40902 | 49.683 | 1.4623 | 0.091998 | 47.3145 | -90.0479 | -85.6026
1349 | 0.11242 | 4.2898 | 1.4078 | 7.1094 | -0.0080206 | -2.8196 | -26709.0669 | -4.2877 | -0.13474 | 49.6827 | 2.8182 | 0.088567 | 47.314 | -90.0363 | -85.6151
1350 | 0.1125 | 2.0633 | 1.3998 | 6.2697 | -0.0086789 | -4.2064 | -26722.0507 | -2.0633 | -7.0763e-15 | 49.6827 | 4.2064 | 1.4426e-14 | 47.3134 | -90.0247 | -85.6258
1351 | 0.11258 | -0.16317 | 1.3911 | 5.4679 | -0.0093812 | -5.6311 | -26708.7275 | 0.16309 | -0.0051254 | 49.683 | 5.6283 | -0.17688 | 47.3126 | -90.0132 | -85.6345
1352 | 0.11267 | -2.3874 | 1.3817 | 4.7116 | -0.010127 | -7.0991 | -26669.1102 | 2.3827 | -0.14991 | 49.6836 | 7.085 | -0.44575 | 47.3118 | -90.0017 | -85.6413
1353 | 0.11275 | -4.6073 | 1.3716 | 4.0077 | -0.010912 | -8.6149 | -26603.2378 | 4.5868 | -0.43358 | 49.6846 | 8.5767 | -0.81074 | 47.3111 | -89.9902 | -85.6462
1354 | 0.11283 | -6.8206 | 1.3607 | 3.3618 | -0.011732 | -10.1824 | -26511.1752 | 6.7668 | -0.85485 | 49.6858 | 10.1021 | -1.2762 | 47.3106 | -89.9789 | -85.6492
1355 | 0.11292 | -9.0251 | 1.349 | 2.7787 | -0.012579 | -11.8038 | -26393.013 | 8.914 | -1.4118 | 49.6874 | 11.6585 | -1.8465 | 47.3104 | -89.9676 | -85.6505
1356 | 0.113 | -11.2187 | 1.3364 | 2.2612 | -0.013443 | -13.4799 | -26248.8676 | 11.02 | -2.1022 | 49.6892 | 13.2411 | -2.5259 | 47.3105 | -89.9564 | -85.65
1357 | 0.11308 | -13.3992 | 1.323 | 1.8102 | -0.014313 | -15.2094 | -26078.8812 | 13.0765 | -2.9229 | 49.6914 | 14.8431 | -3.3178 | 47.311 | -89.9453 | -85.6479
1358 | 0.11317 | -15.5645 | 1.3086 | 1.4249 | -0.015177 | -16.9894 | -25883.2213 | 15.0755 | -3.8707 | 49.6938 | 16.4557 | -4.2251 | 47.312 | -89.9343 | -85.6444
1359 | 0.11325 | -17.7124 | 1.2935 | 1.1024 | -0.016023 | -18.8148 | -25662.0809 | 17.0091 | -4.9416 | 49.6966 | 18.0677 | -5.2492 | 47.3135 | -89.9235 | -85.6396
1360 | 0.11333 | -19.8408 | 1.2774 | 0.838 | -0.01684 | -20.6788 | -25415.678 | 18.8697 | -6.1311 | 49.6996 | 19.6667 | -6.3901 | 47.3155 | -89.9128 | -85.6336
1361 | 0.11342 | -21.9476 | 1.2606 | 0.62583 | -0.01762 | -22.5734 | -25144.2556 | 20.6501 | -7.4345 | 49.7029 | 21.2389 | -7.6465 | 47.318 | -89.9022 | -85.6267
1362 | 0.1135 | -24.0308 | 1.243 | 0.45917 | -0.018357 | -24.49 | -24848.0815 | 22.3433 | -8.8463 | 49.7065 | 22.7702 | -9.0154 | 47.3211 | -89.8918 | -85.6191
1363 | 0.11358 | -26.0883 | 1.2246 | 0.33099 | -0.019049 | -26.4193 | -24527.4478 | 23.9426 | -10.3609 | 49.7104 | 24.2464 | -10.4924 | 47.3247 | -89.8815 | -85.6109
1364 | 0.11367 | -28.118 | 1.2056 | 0.23443 | -0.019695 | -28.3525 | -24182.6707 | 25.442 | -11.9721 | 49.7145 | 25.6541 | -12.0719 | 47.3287 | -89.8714 | -85.6024
1365 | 0.11375 | -30.1181 | 1.1859 | 0.16317 | -0.020296 | -30.2812 | -23814.0903 | 26.8354 | -13.6733 | 49.7189 | 26.9808 | -13.7474 | 47.3331 | -89.8615 | -85.5936
1366 | 0.11383 | -32.0864 | 1.1656 | 0.11161 | -0.020854 | -32.198 | -23422.0702 | 28.1175 | -15.4577 | 49.7236 | 28.2153 | -15.5115 | 47.3379 | -89.8518 | -85.5846
1367 | 0.11392 | -34.0211 | 1.1447 | 0.075026 | -0.021373 | -34.0961 | -23006.9972 | 29.2834 | -17.3181 | 49.7285 | 29.348 | -17.3563 | 47.3431 | -89.8423 | -85.5757
1368 | 0.114 | -35.9203 | 1.1234 | 0.04956 | -0.021855 | -35.9698 | -22569.2806 | 30.3285 | -19.247 | 49.7337 | 30.3703 | -19.2736 | 47.3486 | -89.833 | -85.5668
1369 | 0.11408 | -37.782 | 1.1015 | 0.032168 | -0.022303 | -37.8142 | -22109.3523 | 31.2488 | -21.2366 | 49.7391 | 31.2754 | -21.2547 | 47.3544 | -89.8239 | -85.558
1370 | 0.11417 | -39.6046 | 1.0792 | 0.02051 | -0.022719 | -39.6251 | -21627.666 | 32.0408 | -23.279 | 49.7447 | 32.0573 | -23.291 | 47.3605 | -89.8151 | -85.5494
1371 | 0.11425 | -41.386 | 1.0565 | 0.012843 | -0.023106 | -41.3989 | -21124.697 | 32.7014 | -25.3658 | 49.7505 | 32.7115 | -25.3737 | 47.3668 | -89.8065 | -85.541
1372 | 0.11433 | -43.1248 | 1.0334 | 0.0078959 | -0.023464 | -43.1327 | -20600.9414 | 33.2282 | -27.4888 | 49.7566 | 33.2343 | -27.4938 | 47.3733 | -89.7981 | -85.5328
1373 | 0.11442 | -44.819 | 1.0099 | 0.0047638 | -0.023795 | -44.8237 | -20056.916 | 33.6192 | -29.6393 | 49.7629 | 33.6228 | -29.6425 | 47.3801 | -89.7899 | -85.5249
1374 | 0.1145 | -46.467 | 0.98611 | 0.0028193 | -0.0241 | -46.4698 | -19493.1575 | 33.873 | -31.8089 | 49.7694 | 33.8751 | -31.8108 | 47.387 | -89.782 | -85.5173
1375 | 0.11458 | -48.0673 | 0.96201 | 0.0016358 | -0.024378 | -48.0689 | -18910.222 | 33.9887 | -33.9887 | 49.776 | 33.9899 | -33.9899 | 47.3942 | -89.7744 | -85.5099
1376 | 0.11467 | -49.6182 | 0.93763 | 0.00093001 | -0.024631 | -49.6191 | -18308.6848 | 33.966 | -36.1701 | 49.7829 | 33.9666 | -36.1708 | 47.4015 | -89.7671 | -85.5028
1377 | 0.11475 | -51.1182 | 0.913 | 0.00051778 | -0.024858 | -51.1188 | -17689.1393 | 33.8051 | -38.3444 | 49.7899 | 33.8054 | -38.3448 | 47.409 | -89.76 | -85.496
1378 | 0.11483 | -52.5659 | 0.88814 | 0.0002821 | -0.02506 | -52.5662 | -17052.1968 | 33.5068 | -40.5027 | 49.7971 | 33.507 | -40.503 | 47.4166 | -89.7532 | -85.4896
1379 | 0.11492 | -53.9598 | 0.86308 | 0.00015029 | -0.025236 | -53.96 | -16398.4857 | 33.0724 | -42.6366 | 49.8045 | 33.0724 | -42.6367 | 47.4244 | -89.7466 | -85.4834
1380 | 0.115 | -55.2986 | 0.83785 | 7.8235e-05 | -0.025386 | -55.2986 | -15728.651 | 32.5037 | -44.7375 | 49.8121 | 32.5037 | -44.7375 | 47.4323 | -89.7404 | -85.4775
1381 | 0.11508 | -56.5808 | 0.81246 | 3.9759e-05 | -0.025511 | -56.5809 | -15043.3535 | 31.8031 | -46.7969 | 49.8197 | 31.8032 | -46.7969 | 47.4403 | -89.7345 | -85.472
1382 | 0.11517 | -57.8054 | 0.78695 | 1.9707e-05 | -0.02561 | -57.8054 | -14343.2695 | 30.9737 | -48.8067 | 49.8276 | 30.9737 | -48.8067 | 47.4485 | -89.7288 | -85.4668
1383 | 0.11525 | -58.971 | 0.76134 | 9.5173e-06 | -0.025682 | -58.971 | -13629.0896 | 30.0187 | -50.7588 | 49.8355 | 30.0187 | -50.7588 | 47.4568 | -89.7235 | -85.4619
1384 | 0.11533 | -60.0765 | 0.73566 | 4.4736e-06 | -0.025729 | -60.0765 | -12901.5185 | 28.9421 | -52.6454 | 49.8436 | 28.9421 | -52.6455 | 47.4651 | -89.7184 | -85.4573
1385 | 0.11542 | -61.1209 | 0.70993 | 2.0441e-06 | -0.02575 | -61.1209 | -12161.2741 | 27.7483 | -54.4591 | 49.8518 | 27.7483 | -54.4591 | 47.4736 | -89.7137 | -85.4531
1386 | 0.1155 | -62.1031 | 0.68418 | 9.068e-07 | -0.025745 | -62.1031 | -11409.0868 | 26.4422 | -56.1925 | 49.86 | 26.4422 | -56.1925 | 47.4821 | -89.7093 | -85.4492
1387 | 0.11558 | -63.0221 | 0.65844 | 3.8999e-07 | -0.025714 | -63.0221 | -10645.6987 | 25.0291 | -57.8388 | 49.8684 | 25.0291 | -57.8388 | 47.4908 | -89.7052 | -85.4457
1388 | 0.11567 | -63.8771 | 0.63272 | 1.6234e-07 | -0.025657 | -63.8771 | -9871.8631 | 23.5147 | -59.3914 | 49.8769 | 23.5147 | -59.3914 | 47.4995 | -89.7014 | -85.4425
1389 | 0.11575 | -64.6671 | 0.60706 | 6.5303e-08 | -0.025574 | -64.6671 | -9088.3434 | 21.9052 | -60.8441 | 49.8854 | 21.9052 | -60.8441 | 47.5082 | -89.6979 | -85.4396
1390 | 0.11583 | -65.3915 | 0.58149 | 2.5334e-08 | -0.025465 | -65.3915 | -8295.9128 | 20.2071 | -62.191 | 49.894 | 20.2071 | -62.191 | 47.517 | -89.6947 | -85.4371
1391 | 0.11592 | -66.0496 | 0.55603 | 9.4593e-09 | -0.02533 | -66.0496 | -7495.3532 | 18.4272 | -63.427 | 49.9027 | 18.4272 | -63.427 | 47.5258 | -89.6919 | -85.4349
1392 | 0.116 | -66.6406 | 0.5307 | 3.3914e-09 | -0.02517 | -66.6406 | -6687.4544 | 16.5728 | -64.5469 | 49.9114 | 16.5728 | -64.5469 | 47.5347 | -89.6894 | -85.433
1393 | 0.11608 | -67.1639 | 0.50553 | 1.1645e-09 | -0.024984 | -67.1639 | -5873.0136 | 14.6514 | -65.5464 | 49.9202 | 14.6514 | -65.5464 | 47.5436 | -89.6872 | -85.4315
1394 | 0.11617 | -67.6192 | 0.48054 | 3.8181e-10 | -0.024774 | -67.6192 | -5052.8343 | 12.6706 | -66.4215 | 49.929 | 12.6706 | -66.4215 | 47.5525 | -89.6853 | -85.4303
1395 | 0.11625 | -68.0059 | 0.45577 | 1.1916e-10 | -0.024538 | -68.0059 | -4227.726 | 10.6385 | -67.1687 | 49.9378 | 10.6385 | -67.1687 | 47.5614 | -89.6838 | -85.4295
1396 | 0.11633 | -68.3237 | 0.43123 | 3.5267e-11 | -0.024277 | -68.3237 | -3398.5027 | 8.5632 | -67.785 | 49.9467 | 8.5632 | -67.785 | 47.5703 | -89.6826 | -85.429
1397 | 0.11642 | -68.5723 | 0.40695 | 9.857e-12 | -0.023992 | -68.5723 | -2565.9825 | 6.4532 | -68.2679 | 49.9555 | 6.4532 | -68.2679 | 47.5791 | -89.6817 | -85.4289
1398 | 0.1165 | -68.7513 | 0.38296 | 2.5893e-12 | -0.023682 | -68.7513 | -1730.987 | 4.3169 | -68.6157 | 49.9643 | 4.3169 | -68.6157 | 47.588 | -89.6811 | -85.429
1399 | 0.11658 | -68.8607 | 0.35928 | 6.3572e-13 | -0.023349 | -68.8607 | -894.3401 | 2.163 | -68.8267 | 49.9732 | 2.163 | -68.8267 | 47.5968 | -89.6808 | -85.4296
1400 | 0.11667 | -68.9004 | 0.33593 | 1.4496e-13 | -0.022992 | -68.9004 | -56.8671 | 1.1813e-13 | -68.9004 | 49.982 | 1.1813e-13 | -68.9004 | 47.6056 | -89.6809 | -85.4304
1401 | 0.11675 | -68.8702 | 0.31294 | 3.0469e-14 | -0.022612 | -68.8702 | 780.6054 | -2.1633 | -68.8362 | 49.9908 | -2.1633 | -68.8362 | 47.6143 | -89.6812 | -85.4316
1402 | 0.11683 | -68.7703 | 0.29033 | 5.8516e-15 | -0.022208 | -68.7703 | 1617.2512 | -4.3181 | -68.6346 | 49.9995 | -4.3181 | -68.6346 | 47.623 | -89.6819 | -85.4331
1403 | 0.11692 | -68.6007 | 0.26812 | 1.0161e-15 | -0.021783 | -68.6007 | 2452.2447 | -6.4559 | -68.2963 | 50.0082 | -6.4559 | -68.2963 | 47.6316 | -89.6829 | -85.4349
1404 | 0.117 | -68.3616 | 0.24634 | 1.5753e-16 | -0.021335 | -68.3616 | 3284.7622 | -8.568 | -67.8226 | 50.0168 | -8.568 | -67.8226 | 47.6401 | -89.6842 | -85.437
1405 | 0.11708 | -68.0533 | 0.225 | 2.1468e-17 | -0.020866 | -68.0533 | 4113.982 | -10.6459 | -67.2155 | 50.0254 | -10.6459 | -67.2155 | 47.6486 | -89.6858 | -85.4395
1406 | 0.11717 | -67.6761 | 0.20413 | 2.5231e-18 | -0.020375 | -67.6761 | 4939.086 | -12.6812 | -66.4774 | 50.0339 | -12.6812 | -66.4774 | 47.6569 | -89.6878 | -85.4422
1407 | 0.11725 | -67.2303 | 0.18376 | 2.4961e-19 | -0.019864 | -67.2303 | 5759.2602 | -14.6658 | -65.6112 | 50.0423 | -14.6658 | -65.6112 | 47.6652 | -89.69 | -85.4453
1408 | 0.11733 | -66.7164 | 0.1639 | 2.0149e-20 | -0.019333 | -66.7164 | 6573.6951 | -16.5917 | -64.6204 | 50.0507 | -16.5917 | -64.6204 | 47.6734 | -89.6925 | -85.4487
1409 | 0.11742 | -66.1349 | 0.14456 | 1.2736e-21 | -0.018782 | -66.1349 | 7381.5873 | -18.451 | -63.5089 | 50.0589 | -18.451 | -63.5089 | 47.6814 | -89.6953 | -85.4523
1410 | 0.1175 | -65.4863 | 0.12578 | 5.9612e-23 | -0.018211 | -65.4863 | 8182.1396 | -20.2364 | -62.2812 | 50.0671 | -20.2364 | -62.2812 | 47.6893 | -89.6984 | -85.4563
1411 | 0.11758 | -64.7714 | 0.10757 | 1.9097e-24 | -0.017623 | -64.7714 | 8974.562 | -21.9405 | -60.9422 | 50.0751 | -21.9405 | -60.9422 | 47.6971 | -89.7017 | -85.4605
1412 | 0.11767 | -63.9908 | 0.089947 | 3.7281e-26 | -0.017016 | -63.9908 | 9758.0727 | -23.5566 | -59.4971 | 50.083 | -23.5566 | -59.4971 | 47.7048 | -89.7054 | -85.465
1413 | 0.11775 | -63.1453 | 0.072931 | 3.6968e-28 | -0.016392 | -63.1453 | 10531.8986 | -25.078 | -57.9519 | 50.0908 | -25.078 | -57.9519 | 47.7123 | -89.7093 | -85.4698
1414 | 0.11783 | -62.2358 | 0.056539 | 1.3657e-30 | -0.015752 | -62.2358 | 11295.2761 | -26.4987 | -56.3126 | 50.0985 | -26.4987 | -56.3126 | 47.7197 | -89.7135 | -85.4749
1415 | 0.11792 | -61.2631 | 0.040787 | 1.0357e-33 | -0.015095 | -61.2631 | 12047.4521 | -27.8129 | -54.5858 | 50.106 | -27.8129 | -54.5858 | 47.7269 | -89.7179 | -85.4802
1416 | 0.118 | -60.2282 | 0.025692 | 3.9752e-38 | -0.014423 | -60.2282 | 12787.6844 | -29.0152 | -52.7784 | 50.1134 | -29.0152 | -52.7784 | 47.7339 | -89.7226 | -85.4858
1417 | 0.11808 | -59.1322 | 0.011269 | 5.3164e-46 | -0.013736 | -59.1322 | 13515.2426 | -30.1007 | -50.8975 | 50.1206 | -30.1007 | -50.8975 | 47.7408 | -89.7275 | -85.4916
1418 | 0.11817 | -57.976 | -0.0024662 | -1.6162e-60 | -0.013035 | -57.976 | 14229.4089 | -31.0651 | -48.9508 | 50.1277 | -31.0651 | -48.9508 | 47.7476 | -89.7327 | -85.4976
1419 | 0.11825 | -56.761 | -0.015501 | -5.9095e-43 | -0.01232 | -56.761 | 14929.4785 | -31.9044 | -46.9459 | 50.1346 | -31.9044 | -46.9459 | 47.7541 | -89.7381 | -85.5039
1420 | 0.11833 | -55.4882 | -0.027821 | -2.2904e-37 | -0.011593 | -55.4882 | 15614.7608 | -32.6151 | -44.8909 | 50.1414 | -32.6151 | -44.8909 | 47.7605 | -89.7438 | -85.5104
1421 | 0.11842 | -54.159 | -0.039414 | -4.8752e-34 | -0.010854 | -54.159 | 16284.5795 | -33.1944 | -42.794 | 50.1479 | -33.1944 | -42.794 | 47.7666 | -89.7497 | -85.5172
1422 | 0.1185 | -52.7746 | -0.050267 | -1.0281e-31 | -0.010103 | -52.7746 | 16938.2738 | -33.6398 | -40.6635 | 50.1543 | -33.6398 | -40.6635 | 47.7726 | -89.7557 | -85.5241
1423 | 0.11858 | -51.3364 | -0.06037 | -5.7796e-30 | -0.0093422 | -51.3364 | 17575.1988 | -33.9494 | -38.508 | 50.1605 | -33.9494 | -38.508 | 47.7784 | -89.762 | -85.5312
1424 | 0.11867 | -49.8458 | -0.069713 | -1.3697e-28 | -0.0085714 | -49.8458 | 18194.726 | -34.1218 | -36.336 | 50.1665 | -34.1218 | -36.336 | 47.7839 | -89.7685 | -85.5386
1425 | 0.11875 | -48.3044 | -0.078284 | -1.7562e-27 | -0.0077917 | -48.3044 | 18796.2441 | -34.1564 | -34.1564 | 50.1723 | -34.1564 | -34.1564 | 47.7893 | -89.7752 | -85.5461
1426 | 0.11883 | -46.7136 | -0.086076 | -1.4163e-26 | -0.0070037 | -46.7136 | 19379.1596 | -34.0528 | -31.9777 | 50.1779 | -34.0528 | -31.9777 | 47.7945 | -89.7821 | -85.5538
1427 | 0.11892 | -45.0751 | -0.09308 | -7.9168e-26 | -0.0062083 | -45.0751 | 19942.8975 | -33.8113 | -29.8087 | 50.1833 | -33.8113 | -29.8087 | 47.7994 | -89.7891 | -85.5616
1428 | 0.119 | -43.3904 | -0.099288 | -3.277e-25 | -0.0054063 | -43.3904 | 20486.9014 | -33.4329 | -27.6581 | 50.1885 | -33.4329 | -27.6581 | 47.8041 | -89.7964 | -85.5697
1429 | 0.11908 | -41.6612 | -0.10469 | -1.0521e-24 | -0.0045983 | -41.6612 | 21010.6348 | -32.9188 | -25.5344 | 50.1935 | -32.9188 | -25.5344 | 47.8086 | -89.8038 | -85.5778
1430 | 0.11917 | -39.8892 | -0.10929 | -2.7086e-24 | -0.0037853 | -39.8892 | 21513.5808 | -32.271 | -23.4463 | 50.1983 | -32.271 | -23.4463 | 47.8129 | -89.8113 | -85.5861
1431 | 0.11925 | -38.0762 | -0.11308 | -5.7287e-24 | -0.002968 | -38.0762 | 21995.2433 | -31.4921 | -21.402 | 50.2028 | -31.4921 | -21.402 | 47.8169 | -89.819 | -85.5946
1432 | 0.11933 | -36.2239 | -0.11605 | -1.013e-23 | -0.0021473 | -36.2239 | 22455.147 | -30.5849 | -19.4097 | 50.2071 | -30.5849 | -19.4097 | 47.8207 | -89.8268 | -85.6032
1433 | 0.11942 | -34.3343 | -0.11819 | -1.5163e-23 | -0.0013239 | -34.3343 | 22892.8382 | -29.5529 | -17.4776 | 50.2112 | -29.5529 | -17.4776 | 47.8243 | -89.8347 | -85.6118
1434 | 0.1195 | -32.4091 | -0.11952 | -1.9374e-23 | -0.00049867 | -32.4091 | 23307.8851 | -28.4003 | -15.6132 | 50.2151 | -28.4003 | -15.6132 | 47.8276 | -89.8428 | -85.6206
1435 | 0.11958 | -30.4502 | -0.12002 | -2.1232e-23 | 0.00032756 | -30.4502 | 23699.8783 | -27.1314 | -13.8241 | 50.2187 | -27.1314 | -13.8241 | 47.8307 | -89.851 | -85.6295
1436 | 0.11967 | -28.4597 | -0.11969 | -1.9993e-23 | 0.001154 | -28.4597 | 24068.4309 | -25.7511 | -12.1176 | 50.2221 | -25.7511 | -12.1176 | 47.8335 | -89.8593 | -85.6385
1437 | 0.11975 | -26.4395 | -0.11853 | -1.6155e-23 | 0.0019798 | -26.4395 | 24413.1795 | -24.265 | -10.5004 | 50.2253 | -24.265 | -10.5004 | 47.8361 | -89.8677 | -85.6475
1438 | 0.11983 | -24.3915 | -0.11655 | -1.1153e-23 | 0.0028042 | -24.3915 | 24733.784 | -22.6787 | -8.9791 | 50.2282 | -22.6787 | -8.9791 | 47.8385 | -89.8761 | -85.6567
1439 | 0.11992 | -22.3179 | -0.11375 | -6.5267e-24 | 0.0036264 | -22.3179 | 25029.928 | -20.9985 | -7.5599 | 50.2309 | -20.9985 | -7.5599 | 47.8406 | -89.8847 | -85.6658
1440 | 0.12 | -20.2206 | -0.11012 | -3.1999e-24 | 0.0044454 | -20.2206 | 25301.3195 | -19.2309 | -6.2485 | 50.2333 | -19.2309 | -6.2485 | 47.8425 | -89.8933 | -85.6751
1441 | 0.12008 | -18.1017 | -0.10568 | -1.2925e-24 | 0.0052607 | -18.1017 | 25547.6908 | -17.3829 | -5.0502 | 50.2355 | -17.3829 | -5.0502 | 47.8441 | -89.9019 | -85.6843
1442 | 0.12017 | -15.9633 | -0.10042 | -4.2031e-25 | 0.0060712 | -15.9633 | 25768.7988 | -15.4618 | -3.9699 | 50.2374 | -15.4618 | -3.9699 | 47.8455 | -89.9107 | -85.6936
1443 | 0.12025 | -13.8076 | -0.094346 | -1.0659e-25 | 0.0068763 | -13.8076 | 25964.4255 | -13.4751 | -3.012 | 50.2391 | -13.4751 | -3.012 | 47.8466 | -89.9194 | -85.703
1444 | 0.12033 | -11.6366 | -0.08747 | -2.0168e-26 | 0.0076751 | -11.6366 | 26134.3779 | -11.4305 | -2.1805 | 50.2406 | -11.4305 | -2.1805 | 47.8475 | -89.9282 | -85.7123
1445 | 0.12042 | -9.4526 | -0.079795 | -2.6744e-27 | 0.0084668 | -9.4526 | 26278.4885 | -9.3362 | -1.4787 | 50.2418 | -9.3362 | -1.4787 | 47.8482 | -89.937 | -85.7217
1446 | 0.1205 | -7.2576 | -0.071328 | -2.2673e-28 | 0.0092507 | -7.2576 | 26396.6152 | -7.2004 | -0.90962 | 50.2428 | -7.2004 | -0.90962 | 47.8486 | -89.9459 | -85.731
1447 | 0.12058 | -5.0539 | -0.062078 | -1.0674e-29 | 0.010026 | -5.0539 | 26488.6415 | -5.0315 | -0.47561 | 50.2435 | -5.0315 | -0.47561 | 47.8487 | -89.9547 | -85.7403
1448 | 0.12067 | -2.8436 | -0.052052 | -2.2147e-31 | 0.010792 | -2.8436 | 26554.4767 | -2.838 | -0.17855 | 50.244 | -2.838 | -0.17855 | 47.8486 | -89.9636 | -85.7496
1449 | 0.12075 | -0.62886 | -0.04126 | -1.3347e-33 | 0.011548 | -0.62886 | 26594.0561 | -0.62855 | -0.019753 | 50.2442 | -0.62855 | -0.019753 | 47.8483 | -89.9724 | -85.7589
1450 | 0.12083 | 1.588 | -0.029712 | -9.7356e-37 | 0.012292 | 1.588 | 26607.3406 | 1.588 | 1.1283e-14 | 50.2442 | 1.588 | 1.1283e-14 | 47.8477 | -89.9812 | -85.7681
1451 | 0.12092 | 3.805 | -0.01742 | -7.7052e-42 | 0.013026 | 3.805 | 26594.3173 | 3.8031 | -0.11952 | 50.244 | 3.8031 | -0.11952 | 47.8469 | -89.99 | -85.7773
1452 | 0.121 | 6.0197 | -0.0043943 | -5.3387e-55 | 0.013746 | 6.0197 | 26554.9992 | 6.0078 | -0.37798 | 50.2435 | 6.0078 | -0.37798 | 47.8459 | -89.9987 | -85.7864
1453 | 0.12108 | 8.2301 | 0.0093521 | 8.7856e-48 | 0.014454 | 8.2301 | 26489.4252 | 8.1935 | -0.77452 | 50.2428 | 8.1935 | -0.77452 | 47.8446 | -90.0074 | -85.7955
1454 | 0.12117 | 10.4339 | 0.023806 | 7.4303e-39 | 0.015148 | 10.4339 | 26397.6601 | 10.3516 | -1.3077 | 50.2418 | 10.3516 | -1.3077 | 47.8431 | -90.0161 | -85.8044
1455 | 0.12125 | 12.629 | 0.038955 | 3.7676e-34 | 0.015828 | 12.629 | 26279.7947 | 12.4735 | -1.9756 | 50.2406 | 12.4735 | -1.9756 | 47.8414 | -90.0247 | -85.8133
1456 | 0.12133 | 14.8131 | 0.054783 | 6.8216e-31 | 0.016492 | 14.8131 | 26135.9453 | 14.5507 | -2.7757 | 50.2392 | 14.5507 | -2.7757 | 47.8394 | -90.0332 | -85.8221
1457 | 0.12142 | 16.9842 | 0.071275 | 2.2303e-28 | 0.017141 | 16.9842 | 25966.2541 | 16.5752 | -3.705 | 50.2376 | 16.5752 | -3.705 | 47.8372 | -90.0416 | -85.8308
1458 | 0.1215 | 19.1401 | 0.088416 | 2.5552e-26 | 0.017773 | 19.1401 | 25770.8887 | 18.5388 | -4.76 | 50.2357 | 18.5388 | -4.76 | 47.8348 | -90.05 | -85.8394
1459 | 0.12158 | 21.2787 | 0.10619 | 1.4372e-24 | 0.018388 | 21.2787 | 25550.042 | 20.4338 | -5.9366 | 50.2336 | 20.4338 | -5.9366 | 47.8322 | -90.0583 | -85.8479
1460 | 0.12167 | 23.3978 | 0.12458 | 4.8244e-23 | 0.018986 | 23.3978 | 25303.9321 | 22.2526 | -7.2303 | 50.2313 | 22.2526 | -7.2303 | 47.8293 | -90.0664 | -85.8562
1461 | 0.12175 | 25.4953 | 0.14356 | 1.0933e-21 | 0.019565 | 25.4953 | 25032.8019 | 23.988 | -8.6362 | 50.2287 | 23.988 | -8.6362 | 47.8263 | -90.0745 | -85.8645
1462 | 0.12183 | 27.5692 | 0.16313 | 1.8174e-20 | 0.020126 | 27.5692 | 24736.9192 | 25.6332 | -10.1489 | 50.226 | 25.6332 | -10.1489 | 47.823 | -90.0824 | -85.8725
1463 | 0.12192 | 29.6174 | 0.18325 | 2.3495e-19 | 0.020667 | 29.6174 | 24416.5761 | 27.1815 | -11.7625 | 50.223 | 27.1815 | -11.7625 | 47.8196 | -90.0903 | -85.8805
1464 | 0.122 | 31.638 | 0.20392 | 2.4658e-18 | 0.021188 | 31.638 | 24072.0889 | 28.6269 | -13.4708 | 50.2199 | 28.6269 | -13.4708 | 47.8159 | -90.098 | -85.8883
1465 | 0.12208 | 33.6288 | 0.22511 | 2.1699e-17 | 0.021689 | 33.6288 | 23703.7976 | 29.9635 | -15.2671 | 50.2165 | 29.9635 | -15.2671 | 47.8121 | -90.1055 | -85.8959
1466 | 0.12217 | 35.5879 | 0.2468 | 1.6418e-16 | 0.022169 | 35.5879 | 23312.0659 | 31.186 | -17.1446 | 50.213 | 31.186 | -17.1446 | 47.8081 | -90.1129 | -85.9033
1467 | 0.12225 | 37.5135 | 0.26897 | 1.0894e-15 | 0.022627 | 37.5135 | 22897.2804 | 32.2894 | -19.0959 | 50.2092 | 32.2894 | -19.0959 | 47.8039 | -90.1202 | -85.9106
1468 | 0.12233 | 39.4035 | 0.2916 | 6.4406e-15 | 0.023064 | 39.4035 | 22459.8507 | 33.2695 | -21.1135 | 50.2053 | 33.2695 | -21.1135 | 47.7995 | -90.1273 | -85.9177
1469 | 0.12242 | 41.2562 | 0.31466 | 3.4375e-14 | 0.023478 | 41.2562 | 22000.2085 | 34.1222 | -23.1894 | 50.2012 | 34.1222 | -23.1894 | 47.7949 | -90.1343 | -85.9246
1470 | 0.1225 | 43.0696 | 0.33814 | 1.6742e-13 | 0.02387 | 43.0696 | 21518.8076 | 34.8441 | -25.3157 | 50.1969 | 34.8441 | -25.3157 | 47.7902 | -90.141 | -85.9314
1471 | 0.12258 | 44.8421 | 0.36201 | 7.5083e-13 | 0.024239 | 44.8421 | 21016.1232 | 35.4322 | -27.484 | 50.1924 | 35.4322 | -27.484 | 47.7853 | -90.1477 | -85.9379
1472 | 0.12267 | 46.5717 | 0.38625 | 3.1244e-12 | 0.024584 | 46.5717 | 20492.6515 | 35.8841 | -29.6859 | 50.1878 | 35.8841 | -29.6859 | 47.7803 | -90.1541 | -85.9442
1473 | 0.12275 | 48.2569 | 0.41083 | 1.2143e-11 | 0.024905 | 48.2569 | 19948.9092 | 36.1981 | -31.9129 | 50.183 | 36.1981 | -31.9129 | 47.7751 | -90.1603 | -85.9503
1474 | 0.12283 | 49.896 | 0.43573 | 4.4325e-11 | 0.025202 | 49.896 | 19385.4331 | 36.3726 | -34.1562 | 50.178 | 36.3726 | -34.1562 | 47.7698 | -90.1664 | -85.9563
1475 | 0.12292 | 51.4873 | 0.46094 | 1.5271e-10 | 0.025475 | 51.4873 | 18802.7793 | 36.407 | -36.407 | 50.1729 | 36.407 | -36.407 | 47.7643 | -90.1722 | -85.9619
1476 | 0.123 | 53.0293 | 0.48641 | 4.9872e-10 | 0.025723 | 53.0293 | 18201.523 | 36.301 | -38.6567 | 50.1677 | 36.301 | -38.6567 | 47.7587 | -90.1779 | -85.9674
1477 | 0.12308 | 54.5204 | 0.51214 | 1.5496e-09 | 0.025947 | 54.5204 | 17582.2577 | 36.055 | -40.8964 | 50.1623 | 36.055 | -40.8964 | 47.753 | -90.1834 | -85.9727
1478 | 0.12317 | 55.9592 | 0.53808 | 4.5964e-09 | 0.026145 | 55.9592 | 16945.5946 | 35.6697 | -43.1173 | 50.1568 | 35.6697 | -43.1173 | 47.7472 | -90.1886 | -85.9777
1479 | 0.12325 | 57.3442 | 0.56423 | 1.3054e-08 | 0.026317 | 57.3442 | 16292.1622 | 35.1467 | -45.3108 | 50.1511 | 35.1467 | -45.3108 | 47.7412 | -90.1937 | -85.9824
1480 | 0.12333 | 58.6741 | 0.59054 | 3.5588e-08 | 0.026465 | 58.6741 | 15622.6055 | 34.4878 | -47.4683 | 50.1453 | 34.4878 | -47.4683 | 47.7351 | -90.1985 | -85.987
1481 | 0.12342 | 59.9475 | 0.61701 | 9.3361e-08 | 0.026586 | 59.9475 | 14937.5853 | 33.6955 | -49.5814 | 50.1395 | 33.6955 | -49.5814 | 47.729 | -90.2031 | -85.9913
1482 | 0.1235 | 61.1633 | 0.64359 | 2.3618e-07 | 0.026682 | 61.1633 | 14237.7778 | 32.7729 | -51.6419 | 50.1335 | 32.7729 | -51.6419 | 47.7227 | -90.2074 | -85.9953
1483 | 0.12358 | 62.3201 | 0.67028 | 5.7724e-07 | 0.026752 | 62.3201 | 13523.8737 | 31.7235 | -53.6415 | 50.1274 | 31.7235 | -53.6415 | 47.7164 | -90.2116 | -85.9992
1484 | 0.12367 | 63.4169 | 0.69703 | 1.3655e-06 | 0.026796 | 63.4169 | 12796.5777 | 30.5513 | -55.5726 | 50.1212 | 30.5513 | -55.5726 | 47.71 | -90.2155 | -86.0027
1485 | 0.12375 | 64.4525 | 0.72383 | 3.1312e-06 | 0.026814 | 64.4525 | 12056.6077 | 29.2608 | -57.4276 | 50.1149 | 29.2608 | -57.4276 | 47.7035 | -90.2192 | -86.006
1486 | 0.12383 | 65.426 | 0.75064 | 6.9704e-06 | 0.026806 | 65.426 | 11304.6941 | 27.857 | -59.1992 | 50.1086 | 27.857 | -59.1992 | 47.6969 | -90.2227 | -86.0091
1487 | 0.12392 | 66.3363 | 0.77745 | 1.5084e-05 | 0.026772 | 66.3363 | 10541.5789 | 26.3453 | -60.8805 | 50.1022 | 26.3453 | -60.8805 | 47.6903 | -90.2259 | -86.0119
1488 | 0.124 | 67.1826 | 0.80422 | 3.1768e-05 | 0.026712 | 67.1826 | 9768.0155 | 24.7316 | -62.4648 | 50.0957 | 24.7316 | -62.4648 | 47.6837 | -90.2288 | -86.0144
1489 | 0.12408 | 67.9641 | 0.83093 | 6.5192e-05 | 0.026627 | 67.964 | 8984.7674 | 23.022 | -63.9461 | 50.0891 | 23.022 | -63.946 | 47.6769 | -90.2316 | -86.0167
1490 | 0.12417 | 68.6798 | 0.85756 | 0.00013048 | 0.026515 | 68.6797 | 8192.6076 | 21.2232 | -65.3184 | 50.0825 | 21.2232 | -65.3183 | 47.6702 | -90.2341 | -86.0187
1491 | 0.12425 | 69.3293 | 0.88407 | 0.00025497 | 0.026377 | 69.329 | 7392.318 | 19.3422 | -66.5765 | 50.0759 | 19.3422 | -66.5762 | 47.6634 | -90.2363 | -86.0205
1492 | 0.12433 | 69.9117 | 0.91045 | 0.00048684 | 0.026213 | 69.9112 | 6584.6886 | 17.3863 | -67.7153 | 50.0692 | 17.3862 | -67.7148 | 47.6566 | -90.2383 | -86.022
1493 | 0.12442 | 70.4265 | 0.93666 | 0.00090906 | 0.026023 | 70.4256 | 5770.5165 | 15.3631 | -68.7304 | 50.0624 | 15.3629 | -68.7295 | 47.6499 | -90.2401 | -86.0232
1494 | 0.1245 | 70.8733 | 0.96269 | 0.0016612 | 0.025807 | 70.8716 | 4950.6053 | 13.2803 | -69.6179 | 50.0557 | 13.28 | -69.6163 | 47.6431 | -90.2416 | -86.0242
1495 | 0.12458 | 71.2515 | 0.98849 | 0.0029729 | 0.025565 | 71.2485 | 4125.7642 | 11.1462 | -70.3743 | 50.0489 | 11.1457 | -70.3713 | 47.6363 | -90.2428 | -86.0249
1496 | 0.12467 | 71.5608 | 1.0141 | 0.0052136 | 0.025294 | 71.5556 | 3296.8075 | 8.9689 | -70.9965 | 50.0421 | 8.9683 | -70.9913 | 47.6297 | -90.2439 | -86.0254
1497 | 0.12475 | 71.8009 | 1.0394 | 0.0089648 | 0.024995 | 71.7919 | 2464.5532 | 6.7571 | -71.4822 | 50.0353 | 6.7562 | -71.4733 | 47.6232 | -90.2446 | -86.0256
1498 | 0.12483 | 71.9715 | 1.0643 | 0.015121 | 0.024665 | 71.9564 | 1629.8229 | 4.5191 | -71.8295 | 50.0285 | 4.5182 | -71.8144 | 47.6169 | -90.2451 | -86.0255
1499 | 0.12492 | 72.0725 | 1.089 | 0.025031 | 0.024301 | 72.0474 | 793.4404 | 2.2639 | -72.0369 | 50.0217 | 2.2631 | -72.0119 | 47.6108 | -90.2454 | -86.0252
1500 | 0.125 | 72.1037 | 1.1133 | 0.040677 | 0.0239 | 72.063 | -43.7687 | 3.8862e-13 | -72.1037 | 50.0149 | 3.884e-13 | -72.063 | 47.6053 | -90.2455 | -86.0248
1501 | 0.12508 | 72.0652 | 1.1372 | 0.064906 | 0.023454 | 72.0003 | -880.9781 | -2.2636 | -72.0296 | 50.0082 | -2.2616 | -71.9647 | 47.6004 | -90.2452 | -86.0242
1502 | 0.12517 | 71.9569 | 1.1607 | 0.1017 | 0.022958 | 71.8552 | -1717.3614 | -4.5182 | -71.8149 | 50.0014 | -4.5118 | -71.7134 | 47.5965 | -90.2448 | -86.0236
1503 | 0.12525 | 71.779 | 1.1836 | 0.15649 | 0.0224 | 71.6225 | -2552.0933 | -6.755 | -71.4604 | 49.9947 | -6.7403 | -71.3046 | 47.5939 | -90.2441 | -86.023
1504 | 0.12533 | 71.5316 | 1.206 | 0.23638 | 0.021771 | 71.2952 | -3384.3496 | -8.9653 | -70.9676 | 49.9881 | -8.9357 | -70.7331 | 47.593 | -90.2432 | -86.0228
1505 | 0.12542 | 71.215 | 1.2278 | 0.35038 | 0.021057 | 70.8646 | -4213.3091 | -11.1405 | -70.3382 | 49.9815 | -11.0857 | -69.9922 | 47.5943 | -90.242 | -86.0232
1506 | 0.1255 | 70.8295 | 1.2489 | 0.50935 | 0.020249 | 70.3202 | -5038.1534 | -13.2721 | -69.5749 | 49.9749 | -13.1767 | -69.0746 | 47.5984 | -90.2406 | -86.0245
1507 | 0.12558 | 70.3755 | 1.2691 | 0.72559 | 0.019336 | 69.6499 | -5858.0685 | -15.3519 | -68.6806 | 49.9684 | -15.1936 | -67.9725 | 47.6057 | -90.239 | -86.0271
1508 | 0.12567 | 69.8533 | 1.2884 | 1.012 | 0.018318 | 68.8414 | -6672.2452 | -17.3718 | -67.6588 | 49.962 | -17.1201 | -66.6786 | 47.6167 | -90.2371 | -86.0315
1509 | 0.12575 | 69.2636 | 1.3068 | 1.3805 | 0.0172 | 67.8831 | -7479.8797 | -19.3239 | -66.5134 | 49.9556 | -18.9388 | -65.1877 | 47.6315 | -90.235 | -86.038
1510 | 0.12583 | 68.6069 | 1.324 | 1.8407 | 0.015999 | 66.7662 | -8280.1749 | -21.2007 | -65.249 | 49.9493 | -20.6319 | -63.4984 | 47.6502 | -90.2327 | -86.0471
1511 | 0.12592 | 67.8838 | 1.34 | 2.3975 | 0.01474 | 65.4863 | -9072.341 | -22.9948 | -63.8706 | 49.9431 | -22.1827 | -61.6148 | 47.6726 | -90.2302 | -86.0589
1512 | 0.126 | 67.0951 | 1.3547 | 3.0499 | 0.013456 | 64.0452 | -9855.5961 | -24.6993 | -62.3834 | 49.937 | -23.5766 | -59.5477 | 47.6983 | -90.2274 | -86.0737
1513 | 0.12608 | 66.2415 | 1.3682 | 3.7907 | 0.012179 | 62.4508 | -10629.167 | -26.3077 | -60.7934 | 49.931 | -24.8022 | -57.3145 | 47.727 | -90.2245 | -86.0915
1514 | 0.12617 | 65.3238 | 1.3803 | 4.6067 | 0.010941 | 60.7171 | -11392.2902 | -27.8135 | -59.1068 | 49.925 | -25.8521 | -54.9385 | 47.7579 | -90.2213 | -86.1122
1515 | 0.12625 | 64.3431 | 1.3913 | 5.4806 | 0.0097632 | 58.8625 | -12144.2126 | -29.2111 | -57.3301 | 49.9192 | -26.723 | -52.4469 | 47.7906 | -90.2179 | -86.1356
1516 | 0.12633 | 63.3001 | 1.401 | 6.392 | 0.0086613 | 56.9081 | -12884.1919 | -30.4951 | -55.4703 | 49.9135 | -27.4157 | -49.8689 | 47.8243 | -90.2144 | -86.1615
1517 | 0.12642 | 62.1961 | 1.4097 | 7.3202 | 0.0076425 | 54.8758 | -13611.4978 | -31.6604 | -53.5348 | 49.9079 | -27.9341 | -47.2339 | 47.8587 | -90.2106 | -86.1897
1518 | 0.1265 | 61.0319 | 1.4173 | 8.2448 | 0.0067081 | 52.7871 | -14325.4123 | -32.7025 | -51.531 | 49.9025 | -28.2847 | -44.5696 | 47.8931 | -90.2066 | -86.2198
1519 | 0.12658 | 59.8089 | 1.424 | 9.1473 | 0.005855 | 50.6615 | -15025.2309 | -33.6176 | -49.4668 | 49.8971 | -28.476 | -41.9012 | 47.9272 | -90.2025 | -86.2517
1520 | 0.12667 | 58.5281 | 1.4299 | 10.0115 | 0.0050775 | 48.5166 | -15710.2629 | -34.402 | -47.3502 | 49.8919 | -28.5174 | -39.2508 | 47.9606 | -90.1982 | -86.2849
1521 | 0.12675 | 57.1909 | 1.435 | 10.8235 | 0.0043686 | 46.3675 | -16379.8319 | -35.0527 | -45.1897 | 49.8868 | -28.419 | -36.6375 | 47.9931 | -90.1937 | -86.3192
1522 | 0.12683 | 55.7986 | 1.4393 | 11.572 | 0.0037206 | 44.2266 | -17033.2772 | -35.5674 | -42.9936 | 49.8819 | -28.1911 | -34.0772 | 48.0245 | -90.189 | -86.3544
1523 | 0.12692 | 54.3525 | 1.4431 | 12.2483 | 0.0031261 | 42.1042 | -17669.9538 | -35.944 | -40.7704 | 49.8771 | -27.844 | -31.5829 | 48.0544 | -90.1842 | -86.3902
1524 | 0.127 | 52.8541 | 1.4462 | 12.8455 | 0.002578 | 40.0086 | -18289.2332 | -36.1811 | -38.529 | 49.8724 | -27.3878 | -29.165 | 48.0829 | -90.1792 | -86.4263
1525 | 0.12708 | 51.3048 | 1.4488 | 13.3588 | 0.0020698 | 37.946 | -18890.5042 | -36.278 | -36.278 | 49.8679 | -26.8319 | -26.8319 | 48.1099 | -90.1741 | -86.4627
1526 | 0.12717 | 49.7062 | 1.4508 | 13.785 | 0.0015954 | 35.9212 | -19473.1733 | -36.2343 | -34.0262 | 49.8636 | -26.1854 | -24.5897 | 48.1352 | -90.1688 | -86.499
1527 | 0.12725 | 48.0598 | 1.4524 | 14.1224 | 0.0011497 | 33.9374 | -20036.6653 | -36.0502 | -31.7825 | 49.8594 | -25.4568 | -22.4432 | 48.1588 | -90.1633 | -86.5352
1528 | 0.12733 | 46.3673 | 1.4536 | 14.3704 | 0.00072758 | 31.9969 | -20580.4241 | -35.7266 | -29.5556 | 49.8553 | -24.6541 | -20.3956 | 48.1808 | -90.1578 | -86.571
1529 | 0.12742 | 44.6303 | 1.4543 | 14.5294 | 0.00032485 | 30.1009 | -21103.913 | -35.2649 | -27.3542 | 49.8515 | -23.7843 | -18.449 | 48.2012 | -90.1521 | -86.6063
1530 | 0.1275 | 42.8506 | 1.4546 | 14.601 | -6.2494e-05 | 28.2495 | -21606.6151 | -34.6668 | -25.1869 | 49.8478 | -22.8544 | -16.6047 | 48.2199 | -90.1463 | -86.641
1531 | 0.12758 | 41.0298 | 1.4546 | 14.5872 | -0.00043809 | 26.4426 | -22088.0343 | -33.9349 | -23.0622 | 49.8442 | -21.8701 | -14.8629 | 48.237 | -90.1403 | -86.675
1532 | 0.12767 | 39.1698 | 1.4541 | 14.4909 | -0.00080531 | 24.679 | -22547.6954 | -33.0722 | -20.9882 | 49.8409 | -20.8371 | -13.2236 | 48.2525 | -90.1343 | -86.7082
1533 | 0.12775 | 37.2725 | 1.4533 | 14.3153 | -0.0011673 | 22.9571 | -22985.1447 | -32.082 | -18.9732 | 49.8377 | -19.7602 | -11.6861 | 48.2666 | -90.1281 | -86.7405
1534 | 0.12783 | 35.3396 | 1.4522 | 14.0645 | -0.0015271 | 21.2751 | -23399.9502 | -30.9683 | -17.025 | 49.8347 | -18.6435 | -10.2494 | 48.2792 | -90.1219 | -86.7718
1535 | 0.12792 | 33.3731 | 1.4506 | 13.7427 | -0.0018876 | 19.6304 | -23791.7027 | -29.7357 | -15.1511 | 49.8319 | -17.4908 | -8.912 | 48.2904 | -90.1156 | -86.802
1536 | 0.128 | 31.375 | 1.4488 | 13.3546 | -0.0022517 | 18.0204 | -24160.0153 | -28.3889 | -13.3588 | 49.8293 | -16.3053 | -7.6727 | 48.3003 | -90.1092 | -86.8311
1537 | 0.12808 | 29.3471 | 1.4465 | 12.9053 | -0.0026223 | 16.4418 | -24504.5244 | -26.9334 | -11.6551 | 49.8268 | -15.0895 | -6.5298 | 48.309 | -90.1027 | -86.859
1538 | 0.12817 | 27.2915 | 1.4439 | 12.4003 | -0.0030021 | 14.8912 | -24824.8901 | -25.375 | -10.0467 | 49.8245 | -13.8455 | -5.4818 | 48.3165 | -90.0961 | -86.8856
1539 | 0.12825 | 25.2103 | 1.4409 | 11.8453 | -0.0033942 | 13.365 | -25120.7959 | -23.7199 | -8.5397 | 49.8225 | -12.5749 | -4.5272 | 48.3229 | -90.0895 | -86.911
1540 | 0.12833 | 23.1054 | 1.4375 | 11.2464 | -0.0038015 | 11.859 | -25391.9498 | -21.9746 | -7.14 | 49.8206 | -11.2786 | -3.6646 | 48.3283 | -90.0828 | -86.935
1541 | 0.12842 | 20.979 | 1.4337 | 10.6099 | -0.0042271 | 10.3691 | -25638.0841 | -20.146 | -5.853 | 49.8189 | -9.9574 | -2.8929 | 48.3328 | -90.0761 | -86.9577
1542 | 0.1285 | 18.8331 | 1.4295 | 9.9426 | -0.0046742 | 8.8905 | -25858.9558 | -18.2414 | -4.6836 | 49.8173 | -8.6112 | -2.211 | 48.3364 | -90.0693 | -86.9789
1543 | 0.12858 | 16.6699 | 1.4248 | 9.2514 | -0.0051459 | 7.4185 | -26054.3467 | -16.2684 | -3.6364 | 49.816 | -7.2398 | -1.6183 | 48.3392 | -90.0625 | -86.9987
1544 | 0.12867 | 14.4914 | 1.4196 | 8.5435 | -0.0056455 | 5.9479 | -26224.0641 | -14.2348 | -2.7154 | 49.8149 | -5.8426 | -1.1145 | 48.3413 | -90.0557 | -87.0169
1545 | 0.12875 | 12.2999 | 1.414 | 7.8265 | -0.0061762 | 4.4735 | -26367.9402 | -12.1485 | -1.9241 | 49.8139 | -4.4184 | -0.69981 | 48.3428 | -90.0489 | -87.0337
1546 | 0.12883 | 10.0975 | 1.4078 | 7.1079 | -0.0067407 | 2.9896 | -26485.833 | -10.0179 | -1.2656 | 49.8132 | -2.966 | -0.3747 | 48.3438 | -90.042 | -87.0489
1547 | 0.12892 | 7.8863 | 1.4011 | 6.3956 | -0.0073416 | 1.4907 | -26577.626 | -7.8513 | -0.74217 | 49.8126 | -1.4841 | -0.14029 | 48.3443 | -90.0352 | -87.0625
1548 | 0.129 | 5.6686 | 1.3937 | 5.6975 | -0.0079807 | -0.028901 | -26643.2286 | -5.6574 | -0.35594 | 49.8122 | 0.028844 | 0.0018147 | 48.3444 | -90.0283 | -87.0746
1549 | 0.12908 | 3.4465 | 1.3857 | 5.0213 | -0.0086591 | -1.5748 | -26682.5759 | -3.4448 | -0.10826 | 49.812 | 1.574 | 0.049465 | 48.3442 | -90.0214 | -87.085
1550 | 0.12917 | 1.2223 | 1.3771 | 4.3745 | -0.0093764 | -3.1522 | -26695.629 | -1.2223 | -1.3176e-14 | 49.812 | 3.1522 | 3.3981e-14 | 48.3438 | -90.0146 | -87.0938
1551 | 0.12925 | -1.002 | 1.3677 | 3.764 | -0.010131 | -4.766 | -26682.3749 | 1.0015 | -0.031474 | 49.8122 | 4.7637 | -0.1497 | 48.3433 | -90.0078 | -87.1011
1552 | 0.12933 | -3.2241 | 1.3576 | 3.1961 | -0.010919 | -6.4201 | -26642.8265 | 3.2177 | -0.20244 | 49.8126 | 6.4075 | -0.40312 | 48.3428 | -90.001 | -87.1067
1553 | 0.12942 | -5.4417 | 1.3467 | 2.6758 | -0.011734 | -8.1176 | -26577.0229 | 5.4176 | -0.51211 | 49.8131 | 8.0816 | -0.76393 | 48.3423 | -89.9942 | -87.1108
1554 | 0.1295 | -7.6528 | 1.3349 | 2.2072 | -0.01257 | -9.8601 | -26485.0288 | 7.5925 | -0.95916 | 49.8139 | 9.7823 | -1.2358 | 48.3419 | -89.9875 | -87.1135
1555 | 0.12958 | -9.8552 | 1.3224 | 1.7925 | -0.013417 | -11.6477 | -26366.9349 | 9.7339 | -1.5417 | 49.8148 | 11.5043 | -1.8221 | 48.3416 | -89.9809 | -87.1148
1556 | 0.12967 | -12.0466 | 1.3089 | 1.4322 | -0.014264 | -13.4789 | -26222.8577 | 11.8332 | -2.2573 | 49.8159 | 13.2401 | -2.5257 | 48.3416 | -89.9742 | -87.1148
1557 | 0.12975 | -14.225 | 1.2947 | 1.1254 | -0.015102 | -15.3504 | -26052.9393 | 13.8824 | -3.1031 | 49.8172 | 14.9807 | -3.3486 | 48.3419 | -89.9677 | -87.1136
1558 | 0.12983 | -16.3881 | 1.2796 | 0.86939 | -0.015921 | -17.2574 | -25857.3472 | 15.8732 | -4.0755 | 49.8186 | 16.7153 | -4.2918 | 48.3425 | -89.9612 | -87.1115
1559 | 0.12992 | -18.5338 | 1.2637 | 0.66006 | -0.016713 | -19.1939 | -25636.2744 | 17.7979 | -5.1708 | 49.8202 | 18.4317 | -5.3549 | 48.3434 | -89.9548 | -87.1085
1560 | 0.13 | -20.6601 | 1.2469 | 0.49247 | -0.01747 | -21.1525 | -25389.939 | 19.6489 | -6.3843 | 49.822 | 20.1173 | -6.5365 | 48.3445 | -89.9484 | -87.1048
1561 | 0.13008 | -22.7648 | 1.2295 | 0.36105 | -0.01819 | -23.1258 | -25118.584 | 21.4189 | -7.7113 | 49.824 | 21.7586 | -7.8336 | 48.3461 | -89.9422 | -87.1005
1562 | 0.13017 | -24.8458 | 1.2113 | 0.26011 | -0.01887 | -25.1059 | -24822.477 | 23.1011 | -9.1464 | 49.8261 | 23.3429 | -9.2421 | 48.3479 | -89.936 | -87.0958
1563 | 0.13025 | -26.9012 | 1.1924 | 0.18414 | -0.019509 | -27.0853 | -24501.9102 | 24.6887 | -10.6837 | 49.8284 | 24.8577 | -10.7569 | 48.3499 | -89.93 | -87.0908
1564 | 0.13033 | -28.9288 | 1.1729 | 0.12809 | -0.020109 | -29.0569 | -24157.1999 | 26.1756 | -12.3173 | 49.8309 | 26.2915 | -12.3718 | 48.3523 | -89.924 | -87.0856
1565 | 0.13042 | -30.9267 | 1.1528 | 0.087558 | -0.020672 | -31.0143 | -23788.6861 | 27.5559 | -14.0404 | 49.8335 | 27.6339 | -14.0802 | 48.3549 | -89.9182 | -87.0803
1566 | 0.1305 | -32.8929 | 1.1321 | 0.058804 | -0.021199 | -32.9517 | -23396.7324 | 28.8243 | -15.8463 | 49.8362 | 28.8758 | -15.8746 | 48.3577 | -89.9124 | -87.0749
1567 | 0.13058 | -34.8255 | 1.1109 | 0.038798 | -0.021693 | -34.8643 | -22981.7256 | 29.9758 | -17.7276 | 49.8391 | 30.0092 | -17.7474 | 48.3607 | -89.9068 | -87.0695
1568 | 0.13067 | -36.7226 | 1.0892 | 0.025141 | -0.022156 | -36.7477 | -22544.0751 | 31.0059 | -19.6769 | 49.8422 | 31.0271 | -19.6904 | 48.3639 | -89.9013 | -87.0642
1569 | 0.13075 | -38.5822 | 1.0671 | 0.015997 | -0.02259 | -38.5982 | -22084.2127 | 31.9106 | -21.6864 | 49.8454 | 31.9239 | -21.6954 | 48.3672 | -89.8959 | -87.059
1570 | 0.13083 | -40.4027 | 1.0445 | 0.0099907 | -0.022996 | -40.4127 | -21602.5922 | 32.6865 | -23.7481 | 49.8487 | 32.6945 | -23.754 | 48.3707 | -89.8907 | -87.0539
1571 | 0.13092 | -42.1821 | 1.0215 | 0.006122 | -0.023374 | -42.1882 | -21099.6887 | 33.3304 | -25.8537 | 49.8521 | 33.3352 | -25.8574 | 48.3744 | -89.8856 | -87.0489
1572 | 0.131 | -43.9187 | 0.99811 | 0.0036789 | -0.023727 | -43.9224 | -20575.9985 | 33.84 | -27.9948 | 49.8557 | 33.8428 | -27.9972 | 48.3781 | -89.8806 | -87.044
1573 | 0.13108 | -45.6109 | 0.97439 | 0.0021669 | -0.024054 | -45.613 | -20032.0383 | 34.2132 | -30.163 | 49.8594 | 34.2148 | -30.1644 | 48.382 | -89.8758 | -87.0393
1574 | 0.13117 | -47.2568 | 0.95033 | 0.0012503 | -0.024356 | -47.2581 | -19468.3448 | 34.4488 | -32.3495 | 49.8633 | 34.4497 | -32.3504 | 48.3861 | -89.8711 | -87.0347
1575 | 0.13125 | -48.855 | 0.92598 | 0.00070625 | -0.024632 | -48.8558 | -18885.4742 | 34.5457 | -34.5457 | 49.8672 | 34.5462 | -34.5462 | 48.3902 | -89.8666 | -87.0303
1576 | 0.13133 | -50.4039 | 0.90134 | 0.00039026 | -0.024883 | -50.4043 | -18284.0017 | 34.5038 | -36.7429 | 49.8713 | 34.5041 | -36.7431 | 48.3944 | -89.8623 | -87.026
1577 | 0.13142 | -51.9019 | 0.87646 | 0.0002108 | -0.025109 | -51.9021 | -17664.5208 | 34.3233 | -38.9322 | 49.8755 | 34.3235 | -38.9323 | 48.3988 | -89.8581 | -87.022
1578 | 0.1315 | -53.3475 | 0.85135 | 0.00011121 | -0.02531 | -53.3476 | -17027.6426 | 34.005 | -41.105 | 49.8797 | 34.0051 | -41.105 | 48.4032 | -89.854 | -87.0181
1579 | 0.13158 | -54.7394 | 0.82604 | 5.7253e-05 | -0.025485 | -54.7394 | -16373.9957 | 33.5501 | -43.2526 | 49.8841 | 33.5502 | -43.2526 | 48.4077 | -89.8502 | -87.0143
1580 | 0.13167 | -56.0761 | 0.80056 | 2.8733e-05 | -0.025635 | -56.0761 | -15704.225 | 32.9607 | -45.3665 | 49.8885 | 32.9607 | -45.3665 | 48.4123 | -89.8465 | -87.0108
1581 | 0.13175 | -57.3563 | 0.77492 | 1.4042e-05 | -0.025759 | -57.3563 | -15018.9914 | 32.239 | -47.4383 | 49.8931 | 32.239 | -47.4383 | 48.417 | -89.8429 | -87.0074
1582 | 0.13183 | -58.5788 | 0.74916 | 6.6747e-06 | -0.025857 | -58.5788 | -14318.9711 | 31.3881 | -49.4597 | 49.8977 | 31.3881 | -49.4597 | 48.4218 | -89.8396 | -87.0042
1583 | 0.13192 | -59.7424 | 0.72331 | 3.0821e-06 | -0.025929 | -59.7424 | -13604.8547 | 30.4114 | -51.4228 | 49.9024 | 30.4114 | -51.4228 | 48.4266 | -89.8364 | -87.0013
1584 | 0.132 | -60.8459 | 0.69738 | 1.3805e-06 | -0.025975 | -60.8459 | -12877.347 | 29.3127 | -53.3197 | 49.9072 | 29.3127 | -53.3197 | 48.4315 | -89.8334 | -86.9985
1585 | 0.13208 | -61.8883 | 0.6714 | 5.9893e-07 | -0.025995 | -61.8883 | -12137.1658 | 28.0967 | -55.1429 | 49.912 | 28.0967 | -55.1429 | 48.4365 | -89.8306 | -86.9958
1586 | 0.13217 | -62.8684 | 0.64541 | 2.5125e-07 | -0.025989 | -62.8684 | -11385.0415 | 26.7681 | -56.8851 | 49.9169 | 26.7681 | -56.8851 | 48.4415 | -89.828 | -86.9934
1587 | 0.13225 | -63.7855 | 0.61942 | 1.0172e-07 | -0.025958 | -63.7855 | -10621.7163 | 25.3323 | -58.5394 | 49.9219 | 25.3323 | -58.5394 | 48.4465 | -89.8255 | -86.9912
1588 | 0.13233 | -64.6384 | 0.59346 | 3.9661e-08 | -0.0259 | -64.6384 | -9847.9434 | 23.795 | -60.0993 | 49.9269 | 23.795 | -60.0993 | 48.4516 | -89.8233 | -86.9892
1589 | 0.13242 | -65.4265 | 0.56756 | 1.486e-08 | -0.025816 | -65.4265 | -9064.4863 | 22.1624 | -61.5586 | 49.932 | 22.1624 | -61.5586 | 48.4568 | -89.8212 | -86.9873
1590 | 0.1325 | -66.1489 | 0.54174 | 5.3361e-09 | -0.025707 | -66.1489 | -8272.118 | 20.4411 | -62.9114 | 49.9371 | 20.4411 | -62.9114 | 48.462 | -89.8193 | -86.9857
1591 | 0.13258 | -66.805 | 0.51604 | 1.8312e-09 | -0.025572 | -66.805 | -7471.6206 | 18.638 | -64.1524 | 49.9422 | 18.638 | -64.1524 | 48.4672 | -89.8176 | -86.9843
1592 | 0.13267 | -67.394 | 0.49047 | 5.9861e-10 | -0.025411 | -67.394 | -6663.7839 | 16.7602 | -65.2767 | 49.9474 | 16.7602 | -65.2767 | 48.4724 | -89.8161 | -86.983
1593 | 0.13275 | -67.9154 | 0.46505 | 1.8572e-10 | -0.025224 | -67.9154 | -5849.4049 | 14.8153 | -66.2798 | 49.9526 | 14.8153 | -66.2798 | 48.4776 | -89.8148 | -86.982
1594 | 0.13283 | -68.3687 | 0.43983 | 5.4454e-11 | -0.025013 | -68.3687 | -5029.2875 | 12.811 | -67.1577 | 49.9578 | 12.811 | -67.1577 | 48.4829 | -89.8137 | -86.9811
1595 | 0.13292 | -68.7535 | 0.41482 | 1.5018e-11 | -0.024777 | -68.7535 | -4204.2407 | 10.7554 | -67.907 | 49.963 | 10.7554 | -67.907 | 48.4881 | -89.8128 | -86.9805
1596 | 0.133 | -69.0693 | 0.39004 | 3.8741e-12 | -0.024515 | -69.0693 | -3375.0787 | 8.6567 | -68.5247 | 49.9682 | 8.6567 | -68.5247 | 48.4934 | -89.812 | -86.98
1597 | 0.13308 | -69.3159 | 0.36553 | 9.2885e-13 | -0.024229 | -69.3159 | -2542.6198 | 6.5232 | -69.0083 | 49.9735 | 6.5232 | -69.0083 | 48.4986 | -89.8115 | -86.9798
1598 | 0.13317 | -69.493 | 0.3413 | 2.0542e-13 | -0.023919 | -69.493 | -1707.6854 | 4.3635 | -69.3559 | 49.9787 | 4.3635 | -69.3559 | 48.5039 | -89.8111 | -86.9797
1599 | 0.13325 | -69.6005 | 0.31738 | 4.1535e-14 | -0.023585 | -69.6005 | -871.0994 | 2.1862 | -69.5662 | 49.9839 | 2.1862 | -69.5662 | 48.5091 | -89.811 | -86.9798
1600 | 0.13333 | -69.6382 | 0.29379 | 7.5966e-15 | -0.023228 | -69.6382 | -33.6872 | 6.3126e-13 | -69.6382 | 49.9891 | 6.3126e-13 | -69.6382 | 48.5143 | -89.811 | -86.9801
1601 | 0.13342 | -69.6061 | 0.27056 | 1.2408e-15 | -0.022847 | -69.6061 | 803.7247 | -2.1864 | -69.5718 | 49.9943 | -2.1864 | -69.5718 | 48.5195 | -89.8112 | -86.9807
1602 | 0.1335 | -69.5043 | 0.24772 | 1.7815e-16 | -0.022443 | -69.5043 | 1640.31 | -4.3642 | -69.3671 | 49.9995 | -4.3642 | -69.3671 | 48.5247 | -89.8116 | -86.9814
1603 | 0.13358 | -69.3328 | 0.22527 | 2.205e-17 | -0.022017 | -69.3328 | 2475.2433 | -6.5248 | -69.0251 | 50.0047 | -6.5248 | -69.0251 | 48.5298 | -89.8122 | -86.9823
1604 | 0.13367 | -69.0918 | 0.20326 | 2.295e-18 | -0.021568 | -69.0918 | 3307.7006 | -8.6595 | -68.547 | 50.0098 | -8.6595 | -68.547 | 48.5349 | -89.8129 | -86.9833
1605 | 0.13375 | -68.7816 | 0.18169 | 1.9454e-19 | -0.021098 | -68.7816 | 4136.8605 | -10.7598 | -67.9348 | 50.0149 | -10.7598 | -67.9348 | 48.5399 | -89.8139 | -86.9846
1606 | 0.13383 | -68.4024 | 0.16059 | 1.2871e-20 | -0.020607 | -68.4024 | 4961.9047 | -12.8173 | -67.1908 | 50.0199 | -12.8173 | -67.1908 | 48.5449 | -89.815 | -86.9861
1607 | 0.13392 | -67.9547 | 0.13998 | 6.2729e-22 | -0.020095 | -67.9547 | 5782.0192 | -14.8239 | -66.3182 | 50.0249 | -14.8239 | -66.3182 | 48.5498 | -89.8163 | -86.9877
1608 | 0.134 | -67.4389 | 0.11989 | 2.0742e-23 | -0.019563 | -67.4389 | 6596.3946 | -16.7714 | -65.3202 | 50.0299 | -16.7714 | -65.3202 | 48.5547 | -89.8178 | -86.9895
1609 | 0.13408 | -66.8555 | 0.10032 | 4.1187e-25 | -0.019012 | -66.8555 | 7404.2274 | -18.6521 | -64.2009 | 50.0347 | -18.6521 | -64.2009 | 48.5595 | -89.8194 | -86.9915
1610 | 0.13417 | -66.2051 | 0.081313 | 4.0485e-27 | -0.018441 | -66.2051 | 8204.7205 | -20.4585 | -62.9648 | 50.0396 | -20.4585 | -62.9648 | 48.5643 | -89.8212 | -86.9936
1611 | 0.13425 | -65.4883 | 0.062872 | 1.412e-29 | -0.017852 | -65.4883 | 8997.0839 | -22.1834 | -61.6167 | 50.0443 | -22.1834 | -61.6167 | 48.5689 | -89.8232 | -86.9959
1612 | 0.13433 | -64.7058 | 0.04502 | 9.0935e-33 | -0.017245 | -64.7058 | 9780.5357 | -23.8198 | -60.162 | 50.049 | -23.8198 | -60.162 | 48.5735 | -89.8253 | -86.9984
1613 | 0.13442 | -63.8585 | 0.027776 | 2.2098e-37 | -0.01662 | -63.8585 | 10554.3028 | -25.3613 | -58.6064 | 50.0537 | -25.3613 | -58.6064 | 48.5781 | -89.8277 | -87.0011
1614 | 0.1345 | -62.9471 | 0.011155 | 4.2507e-46 | -0.015979 | -62.9471 | 11317.6218 | -26.8016 | -56.9562 | 50.0582 | -26.8016 | -56.9562 | 48.5825 | -89.8301 | -87.0039
1615 | 0.13458 | -61.9725 | -0.0048234 | -4.1457e-54 | -0.015322 | -61.9725 | 12069.7394 | -28.1349 | -55.2179 | 50.0627 | -28.1349 | -55.2179 | 48.5868 | -89.8327 | -87.0068
1616 | 0.13467 | -60.9358 | -0.020145 | -1.8854e-40 | -0.014649 | -60.9358 | 12809.9134 | -29.356 | -53.3984 | 50.067 | -29.356 | -53.3984 | 48.5911 | -89.8355 | -87.0099
1617 | 0.13475 | -59.8379 | -0.034794 | -3.1388e-35 | -0.013961 | -59.8379 | 13537.4135 | -30.46 | -51.505 | 50.0713 | -30.46 | -51.505 | 48.5952 | -89.8384 | -87.0132
1618 | 0.13483 | -58.6799 | -0.048755 | -5.2497e-32 | -0.013259 | -58.6799 | 14251.5218 | -31.4423 | -49.5451 | 50.0755 | -31.4423 | -49.5451 | 48.5993 | -89.8415 | -87.0166
1619 | 0.13492 | -57.463 | -0.062014 | -1.0437e-29 | -0.012544 | -57.463 | 14951.5336 | -32.299 | -47.5265 | 50.0796 | -32.299 | -47.5265 | 48.6033 | -89.8447 | -87.0201
1620 | 0.135 | -56.1884 | -0.074558 | -6.0075e-28 | -0.011817 | -56.1884 | 15636.7582 | -33.0267 | -45.4574 | 50.0836 | -33.0267 | -45.4574 | 48.6071 | -89.848 | -87.0238
1621 | 0.13508 | -54.8573 | -0.086375 | -1.5286e-26 | -0.011077 | -54.8573 | 16306.5194 | -33.6224 | -43.3458 | 50.0875 | -33.6224 | -43.3458 | 48.6108 | -89.8515 | -87.0276
1622 | 0.13517 | -53.4711 | -0.097452 | -2.1733e-25 | -0.010326 | -53.4711 | 16960.1564 | -34.0838 | -41.2002 | 50.0913 | -34.0838 | -41.2002 | 48.6145 | -89.8551 | -87.0315
1623 | 0.13525 | -52.0311 | -0.10778 | -1.9924e-24 | -0.0095641 | -52.0311 | 17597.0242 | -34.4088 | -39.0291 | 50.095 | -34.4088 | -39.0291 | 48.618 | -89.8589 | -87.0356
1624 | 0.13533 | -50.5387 | -0.11734 | -1.2933e-23 | -0.0087928 | -50.5387 | 18216.4943 | -34.5961 | -36.8412 | 50.0985 | -34.5961 | -36.8412 | 48.6214 | -89.8627 | -87.0397
1625 | 0.13542 | -48.9955 | -0.12613 | -6.34e-23 | -0.0080125 | -48.9955 | 18817.9554 | -34.6451 | -34.6451 | 50.102 | -34.6451 | -34.6451 | 48.6246 | -89.8667 | -87.044
1626 | 0.1355 | -47.4029 | -0.13415 | -2.4577e-22 | -0.0072239 | -47.4029 | 19400.8142 | -34.5552 | -32.4495 | 50.1053 | -34.5552 | -32.4495 | 48.6278 | -89.8707 | -87.0484
1627 | 0.13558 | -45.7626 | -0.14137 | -7.7923e-22 | -0.0064279 | -45.7626 | 19964.4954 | -34.327 | -30.2633 | 50.1085 | -34.327 | -30.2633 | 48.6308 | -89.8749 | -87.0529
1628 | 0.13567 | -44.0761 | -0.1478 | -2.0726e-21 | -0.0056253 | -44.0761 | 20508.4429 | -33.9612 | -28.0951 | 50.1116 | -33.9612 | -28.0951 | 48.6337 | -89.8792 | -87.0575
1629 | 0.13575 | -42.3451 | -0.15342 | -4.7142e-21 | -0.0048168 | -42.3451 | 21032.12 | -33.4592 | -25.9536 | 50.1146 | -33.4592 | -25.9536 | 48.6365 | -89.8836 | -87.0621
1630 | 0.13583 | -40.5713 | -0.15824 | -9.3059e-21 | -0.0040032 | -40.5713 | 21535.0098 | -32.8229 | -23.8472 | 50.1174 | -32.8229 | -23.8472 | 48.6391 | -89.888 | -87.0669
1631 | 0.13592 | -38.7565 | -0.16224 | -1.6124e-20 | -0.0031853 | -38.7565 | 22016.6162 | -32.0547 | -21.7844 | 50.1201 | -32.0547 | -21.7844 | 48.6416 | -89.8926 | -87.0717
1632 | 0.136 | -36.9025 | -0.16543 | -2.473e-20 | -0.002364 | -36.9025 | 22476.4641 | -31.1578 | -19.7733 | 50.1226 | -31.1578 | -19.7733 | 48.644 | -89.8972 | -87.0767
1633 | 0.13608 | -35.011 | -0.16779 | -3.3791e-20 | -0.0015401 | -35.011 | 22914.0996 | -30.1355 | -17.8221 | 50.1251 | -30.1355 | -17.8221 | 48.6462 | -89.9019 | -87.0817
1634 | 0.13617 | -33.0841 | -0.16933 | -4.1314e-20 | -0.0007143 | -33.0841 | 23329.0909 | -28.9918 | -15.9384 | 50.1274 | -28.9918 | -15.9384 | 48.6483 | -89.9067 | -87.0867
1635 | 0.13625 | -31.1235 | -0.17005 | -4.5323e-20 | 0.0001125 | -31.1235 | 23721.0286 | -27.7312 | -14.1298 | 50.1295 | -27.7312 | -14.1298 | 48.6502 | -89.9116 | -87.0918
1636 | 0.13633 | -29.1312 | -0.16994 | -4.4668e-20 | 0.0009395 | -29.1312 | 24089.526 | -26.3587 | -12.4035 | 50.1315 | -26.3587 | -12.4035 | 48.652 | -89.9165 | -87.097
1637 | 0.13642 | -27.1092 | -0.169 | -3.9539e-20 | 0.0017659 | -27.1092 | 24434.2194 | -24.8796 | -10.7664 | 50.1334 | -24.8796 | -10.7664 | 48.6537 | -89.9215 | -87.1022
1638 | 0.1365 | -25.0595 | -0.16723 | -3.138e-20 | 0.0025908 | -25.0595 | 24754.7689 | -23.2997 | -9.225 | 50.1351 | -23.2997 | -9.225 | 48.6552 | -89.9265 | -87.1075
1639 | 0.13658 | -22.9841 | -0.16464 | -2.2258e-20 | 0.0034135 | -22.9841 | 25050.858 | -21.6253 | -7.7856 | 50.1367 | -21.6253 | -7.7856 | 48.6566 | -89.9315 | -87.1128
1640 | 0.13667 | -20.8851 | -0.16123 | -1.4038e-20 | 0.0042332 | -20.8851 | 25322.1948 | -19.8629 | -6.4538 | 50.1382 | -19.8629 | -6.4538 | 48.6578 | -89.9367 | -87.1181
1641 | 0.13675 | -18.7644 | -0.15699 | -7.8177e-21 | 0.005049 | -18.7644 | 25568.5115 | -18.0194 | -5.2351 | 50.1395 | -18.0194 | -5.2351 | 48.6589 | -89.9418 | -87.1235
1642 | 0.13683 | -16.6243 | -0.15194 | -3.8085e-21 | 0.00586 | -16.6243 | 25789.5651 | -16.1021 | -4.1343 | 50.1406 | -16.1021 | -4.1343 | 48.6598 | -89.947 | -87.1289
1643 | 0.13692 | -14.4669 | -0.14608 | -1.6031e-21 | 0.0066657 | -14.4669 | 25985.1375 | -14.1185 | -3.1559 | 50.1417 | -14.1185 | -3.1559 | 48.6606 | -89.9522 | -87.1343
1644 | 0.137 | -12.2942 | -0.13942 | -5.7378e-22 | 0.007465 | -12.2942 | 26155.0357 | -12.0764 | -2.3037 | 50.1425 | -12.0764 | -2.3037 | 48.6612 | -89.9574 | -87.1397
1645 | 0.13708 | -10.1084 | -0.13195 | -1.7098e-22 | 0.0082573 | -10.1084 | 26299.0923 | -9.984 | -1.5813 | 50.1432 | -9.984 | -1.5813 | 48.6617 | -89.9626 | -87.1452
1646 | 0.13717 | -7.9117 | -0.1237 | -4.126e-23 | 0.0090417 | -7.9117 | 26417.1651 | -7.8494 | -0.9916 | 50.1438 | -7.8494 | -0.9916 | 48.6621 | -89.9679 | -87.1506
1647 | 0.13725 | -5.7063 | -0.11465 | -7.7676e-24 | 0.0098175 | -5.7063 | 26509.1377 | -5.681 | -0.53701 | 50.1443 | -5.681 | -0.53701 | 48.6623 | -89.9731 | -87.156
1648 | 0.13733 | -3.4943 | -0.10484 | -1.0839e-24 | 0.010584 | -3.4943 | 26574.9194 | -3.4874 | -0.21941 | 50.1445 | -3.4874 | -0.21941 | 48.6623 | -89.9784 | -87.1614
1649 | 0.13742 | -1.2779 | -0.094252 | -1.0427e-25 | 0.01134 | -1.2779 | 26614.4453 | -1.2772 | -0.040139 | 50.1447 | -1.2772 | -0.040139 | 48.6623 | -89.9836 | -87.1668
1650 | 0.1375 | 0.94073 | -0.082912 | -6.2135e-27 | 0.012086 | 0.94073 | 26627.6765 | 0.94073 | 1.3598e-14 | 50.1447 | 0.94073 | 1.3598e-14 | 48.662 | -89.9888 | -87.1722
1651 | 0.13758 | 3.1593 | -0.070826 | -1.9411e-28 | 0.012819 | 3.1593 | 26614.6 | 3.1578 | -0.099237 | 50.1445 | 3.1578 | -0.099237 | 48.6617 | -89.9941 | -87.1776
1652 | 0.13767 | 5.3758 | -0.058007 | -2.4006e-30 | 0.013541 | 5.3758 | 26575.2289 | 5.3652 | -0.33755 | 50.1443 | 5.3652 | -0.33755 | 48.6612 | -89.9992 | -87.1829
1653 | 0.13775 | 7.5878 | -0.044466 | -6.925e-33 | 0.014249 | 7.5878 | 26509.602 | 7.5541 | -0.71408 | 50.1438 | 7.5541 | -0.71408 | 48.6605 | -90.0044 | -87.1882
1654 | 0.13783 | 9.7933 | -0.030217 | -1.4103e-36 | 0.014944 | 9.7933 | 26417.7841 | 9.7161 | -1.2274 | 50.1433 | 9.7161 | -1.2274 | 48.6597 | -90.0095 | -87.1935
1655 | 0.13792 | 11.9901 | -0.015273 | -4.2695e-43 | 0.015624 | 11.9901 | 26299.8661 | 11.8424 | -1.8757 | 50.1426 | 11.8424 | -1.8757 | 48.6588 | -90.0146 | -87.1987
1656 | 0.138 | 14.1759 | 0.00035033 | 3.6497e-79 | 0.016289 | 14.1759 | 26155.9642 | 13.9248 | -2.6563 | 50.1417 | 13.9248 | -2.6563 | 48.6577 | -90.0197 | -87.2038
1657 | 0.13808 | 16.3487 | 0.016639 | 2.8094e-42 | 0.016938 | 16.3487 | 25986.2207 | 15.9549 | -3.5664 | 50.1407 | 15.9549 | -3.5664 | 48.6565 | -90.0247 | -87.2089
1658 | 0.13817 | 18.5062 | 0.033577 | 1.4345e-35 | 0.017571 | 18.5062 | 25790.8031 | 17.9248 | -4.6023 | 50.1396 | 17.9248 | -4.6023 | 48.6552 | -90.0297 | -87.214
1659 | 0.13825 | 20.6464 | 0.051148 | 1.5065e-31 | 0.018187 | 20.6464 | 25569.9043 | 19.8266 | -5.7602 | 50.1384 | 19.8266 | -5.7602 | 48.6538 | -90.0346 | -87.2189
1660 | 0.13833 | 22.7672 | 0.069334 | 1.2152e-28 | 0.018785 | 22.7672 | 25323.7424 | 21.6529 | -7.0354 | 50.137 | 21.6529 | -7.0354 | 48.6522 | -90.0394 | -87.2239
1661 | 0.13842 | 24.8664 | 0.088119 | 2.373e-26 | 0.019364 | 24.8664 | 25052.5605 | 23.3963 | -8.4232 | 50.1355 | 23.3963 | -8.4232 | 48.6505 | -90.0442 | -87.2287
1662 | 0.1385 | 26.9419 | 0.10748 | 1.8762e-24 | 0.019925 | 26.9419 | 24756.6261 | 25.05 | -9.918 | 50.1339 | 25.05 | -9.918 | 48.6486 | -90.0489 | -87.2335
1663 | 0.13858 | 28.9918 | 0.12741 | 7.9097e-23 | 0.020467 | 28.9918 | 24436.2315 | 26.6073 | -11.514 | 50.1321 | 26.6073 | -11.514 | 48.6467 | -90.0536 | -87.2381
1664 | 0.13867 | 31.0139 | 0.14788 | 2.0966e-21 | 0.020989 | 31.0139 | 24091.6929 | 28.0623 | -13.2051 | 50.1302 | 28.0623 | -13.2051 | 48.6446 | -90.0581 | -87.2427
1665 | 0.13875 | 33.0064 | 0.16886 | 3.8871e-20 | 0.02149 | 33.0064 | 23723.3504 | 29.4089 | -14.9846 | 50.1282 | 29.4089 | -14.9846 | 48.6424 | -90.0626 | -87.2472
1666 | 0.13883 | 34.9672 | 0.19036 | 5.4222e-19 | 0.021971 | 34.9672 | 23331.5675 | 30.642 | -16.8456 | 50.1261 | 30.642 | -16.8456 | 48.6401 | -90.067 | -87.2516
1667 | 0.13892 | 36.8944 | 0.21233 | 5.9953e-18 | 0.02243 | 36.8944 | 22916.7311 | 31.7565 | -18.7808 | 50.1239 | 31.7565 | -18.7808 | 48.6377 | -90.0713 | -87.2559
1668 | 0.139 | 38.786 | 0.23476 | 5.4613e-17 | 0.022867 | 38.786 | 22479.2505 | 32.7481 | -20.7826 | 50.1216 | 32.7481 | -20.7826 | 48.6352 | -90.0755 | -87.2601
1669 | 0.13908 | 40.6403 | 0.25762 | 4.2206e-16 | 0.023282 | 40.6403 | 22019.5576 | 33.6128 | -22.8432 | 50.1191 | 33.6128 | -22.8432 | 48.6326 | -90.0797 | -87.2642
1670 | 0.13917 | 42.4553 | 0.2809 | 2.8315e-15 | 0.023674 | 42.4553 | 21538.1061 | 34.3471 | -24.9546 | 50.1166 | 34.3471 | -24.9546 | 48.6299 | -90.0837 | -87.2682
1671 | 0.13925 | 44.2294 | 0.30458 | 1.6792e-14 | 0.024043 | 44.2294 | 21035.3712 | 34.9481 | -27.1085 | 50.1139 | 34.9481 | -27.1085 | 48.6271 | -90.0876 | -87.2721
1672 | 0.13933 | 45.9607 | 0.32862 | 8.9336e-14 | 0.024388 | 45.9607 | 20511.8492 | 35.4133 | -29.2964 | 50.1112 | 35.4133 | -29.2964 | 48.6242 | -90.0914 | -87.2759
1673 | 0.13942 | 47.6475 | 0.35301 | 4.3155e-13 | 0.02471 | 47.6475 | 19968.0567 | 35.7409 | -31.5098 | 50.1083 | 35.7409 | -31.5098 | 48.6212 | -90.0951 | -87.2795
1674 | 0.1395 | 49.2881 | 0.37772 | 1.9119e-12 | 0.025008 | 49.2881 | 19404.5305 | 35.9295 | -33.74 | 50.1054 | 35.9295 | -33.74 | 48.6181 | -90.0987 | -87.283
1675 | 0.13958 | 50.881 | 0.40273 | 7.8341e-12 | 0.025281 | 50.881 | 18821.8268 | 35.9783 | -35.9783 | 50.1024 | 35.9783 | -35.9783 | 48.6149 | -90.1022 | -87.2864
1676 | 0.13967 | 52.4246 | 0.42801 | 2.9902e-11 | 0.02553 | 52.4246 | 18220.5207 | 35.8871 | -38.2159 | 50.0993 | 35.8871 | -38.2159 | 48.6117 | -90.1055 | -87.2897
1677 | 0.13975 | 53.9173 | 0.45354 | 1.0697e-10 | 0.025754 | 53.9173 | 17601.2057 | 35.6561 | -40.4439 | 50.0961 | 35.6561 | -40.4439 | 48.6083 | -90.1088 | -87.2929
1678 | 0.13983 | 55.3576 | 0.47929 | 3.6055e-10 | 0.025952 | 55.3576 | 16964.4931 | 35.2863 | -42.6538 | 50.0928 | 35.2863 | -42.6538 | 48.6049 | -90.1119 | -87.2959
1679 | 0.13992 | 56.7442 | 0.50524 | 1.1503e-09 | 0.026126 | 56.7442 | 16311.0113 | 34.7789 | -44.8367 | 50.0894 | 34.7789 | -44.8367 | 48.6014 | -90.1149 | -87.2987
1680 | 0.14 | 58.0757 | 0.53137 | 3.4874e-09 | 0.026274 | 58.0757 | 15641.4053 | 34.136 | -46.9842 | 50.086 | 34.136 | -46.9842 | 48.5979 | -90.1177 | -87.3015
1681 | 0.14008 | 59.3507 | 0.55764 | 1.0084e-08 | 0.026396 | 59.3507 | 14956.3359 | 33.36 | -49.0878 | 50.0825 | 33.36 | -49.0878 | 48.5943 | -90.1204 | -87.3041
1682 | 0.14017 | 60.568 | 0.58404 | 2.7893e-08 | 0.026492 | 60.568 | 14256.4794 | 32.4539 | -51.1392 | 50.079 | 32.4539 | -51.1392 | 48.5907 | -90.123 | -87.3065
1683 | 0.14025 | 61.7264 | 0.61053 | 7.4019e-08 | 0.026563 | 61.7264 | 13542.5264 | 31.4213 | -53.1305 | 50.0754 | 31.4213 | -53.1305 | 48.5869 | -90.1255 | -87.3089
1684 | 0.14033 | 62.8247 | 0.63709 | 1.889e-07 | 0.026607 | 62.8247 | 12815.1817 | 30.266 | -55.0537 | 50.0717 | 30.266 | -55.0537 | 48.5832 | -90.1278 | -87.311
1685 | 0.14042 | 63.8619 | 0.6637 | 4.6469e-07 | 0.026626 | 63.8619 | 12075.163 | 28.9927 | -56.9014 | 50.068 | 28.9927 | -56.9014 | 48.5794 | -90.13 | -87.3131
1686 | 0.1405 | 64.8369 | 0.69033 | 1.104e-06 | 0.026618 | 64.8369 | 11323.2009 | 27.6062 | -58.6662 | 50.0642 | 27.6062 | -58.6662 | 48.5755 | -90.132 | -87.3149
1687 | 0.14058 | 65.7488 | 0.71695 | 2.5378e-06 | 0.026585 | 65.7488 | 10560.0373 | 26.112 | -60.3412 | 50.0604 | 26.112 | -60.3412 | 48.5716 | -90.1339 | -87.3167
1688 | 0.14067 | 66.5966 | 0.74353 | 5.6537e-06 | 0.026525 | 66.5966 | 9786.4257 | 24.5158 | -61.92 | 50.0566 | 24.5158 | -61.92 | 48.5677 | -90.1357 | -87.3183
1689 | 0.14075 | 67.3796 | 0.77006 | 1.2225e-05 | 0.02644 | 67.3796 | 9003.1294 | 22.824 | -63.3961 | 50.0527 | 22.824 | -63.3961 | 48.5638 | -90.1373 | -87.3197
1690 | 0.14083 | 68.0969 | 0.7965 | 2.5692e-05 | 0.026329 | 68.0969 | 8210.9216 | 21.0431 | -64.764 | 50.0488 | 21.0431 | -64.764 | 48.5598 | -90.1387 | -87.321
1691 | 0.14092 | 68.7478 | 0.82282 | 5.2544e-05 | 0.026192 | 68.7478 | 7410.5842 | 19.18 | -66.0181 | 50.0448 | 19.18 | -66.0181 | 48.5558 | -90.1401 | -87.3221
1692 | 0.141 | 69.3318 | 0.84902 | 0.00010469 | 0.026029 | 69.3317 | 6602.907 | 17.2421 | -67.1536 | 50.0409 | 17.2421 | -67.1535 | 48.5518 | -90.1413 | -87.3231
1693 | 0.14108 | 69.8481 | 0.87505 | 0.00020344 | 0.025841 | 69.8479 | 5788.6872 | 15.2369 | -68.166 | 50.0369 | 15.2369 | -68.1658 | 48.5478 | -90.1423 | -87.3239
1694 | 0.14117 | 70.2964 | 0.90089 | 0.00038593 | 0.025627 | 70.296 | 4968.7285 | 13.1722 | -69.0513 | 50.0329 | 13.1722 | -69.0509 | 48.5437 | -90.1432 | -87.3246
1695 | 0.14125 | 70.6761 | 0.92651 | 0.00071533 | 0.025388 | 70.6754 | 4143.8401 | 11.0562 | -69.806 | 50.0289 | 11.0561 | -69.8053 | 48.5397 | -90.1439 | -87.3251
1696 | 0.14133 | 70.9869 | 0.9519 | 0.0012966 | 0.025123 | 70.9856 | 3314.8361 | 8.897 | -70.4272 | 50.0248 | 8.8969 | -70.4259 | 48.5357 | -90.1445 | -87.3255
1697 | 0.14142 | 71.2285 | 0.97703 | 0.0022998 | 0.024833 | 71.2262 | 2482.5347 | 6.7032 | -70.9124 | 50.0208 | 6.703 | -70.9101 | 48.5317 | -90.145 | -87.3257
1698 | 0.1415 | 71.4006 | 1.0019 | 0.0039949 | 0.024516 | 71.3966 | 1647.7573 | 4.4833 | -71.2597 | 50.0168 | 4.483 | -71.2557 | 48.5277 | -90.1453 | -87.3258
1699 | 0.14158 | 71.5031 | 1.0264 | 0.0067997 | 0.024172 | 71.4963 | 811.328 | 2.246 | -71.4678 | 50.0127 | 2.2458 | -71.461 | 48.5238 | -90.1454 | -87.3257
1700 | 0.14167 | 71.5358 | 1.0505 | 0.011347 | 0.0238 | 71.5245 | -25.9279 | 4.0308e-13 | -71.5358 | 50.0087 | 4.0301e-13 | -71.5245 | 48.52 | -90.1454 | -87.3255
1701 | 0.14175 | 71.4988 | 1.0743 | 0.018575 | 0.023398 | 71.4802 | -863.184 | -2.2458 | -71.4635 | 50.0047 | -2.2452 | -71.4449 | 48.5164 | -90.1453 | -87.3252
1702 | 0.14183 | 71.392 | 1.0977 | 0.029839 | 0.022963 | 71.3621 | -1699.6138 | -4.4827 | -71.2511 | 50.0007 | -4.4809 | -71.2213 | 48.5129 | -90.145 | -87.3247
1703 | 0.14192 | 71.2155 | 1.1207 | 0.047054 | 0.022492 | 71.1685 | -2534.3921 | -6.702 | -70.8995 | 49.9968 | -6.6975 | -70.8526 | 48.5097 | -90.1446 | -87.3242
1704 | 0.142 | 70.9696 | 1.1432 | 0.072853 | 0.02198 | 70.8968 | -3366.6947 | -8.8949 | -70.41 | 49.9928 | -8.8857 | -70.3377 | 48.507 | -90.144 | -87.3236
1705 | 0.14208 | 70.6545 | 1.1652 | 0.11077 | 0.021422 | 70.5437 | -4195.7003 | -11.0528 | -69.7846 | 49.9889 | -11.0355 | -69.6752 | 48.5047 | -90.1433 | -87.3231
1706 | 0.14217 | 70.2705 | 1.1866 | 0.16538 | 0.02081 | 70.1051 | -5020.5907 | -13.1674 | -69.0258 | 49.985 | -13.1364 | -68.8633 | 48.5033 | -90.1425 | -87.3227
1707 | 0.14225 | 69.8179 | 1.2074 | 0.24243 | 0.020138 | 69.5755 | -5840.5517 | -15.2303 | -68.1364 | 49.9812 | -15.1774 | -67.8999 | 48.5027 | -90.1415 | -87.3225
1708 | 0.14233 | 69.2972 | 1.2276 | 0.34884 | 0.019397 | 68.9484 | -6654.7742 | -17.2335 | -67.1201 | 49.9774 | -17.1468 | -66.7822 | 48.5035 | -90.1404 | -87.3228
1709 | 0.14242 | 68.7089 | 1.2469 | 0.49252 | 0.018583 | 68.2164 | -7462.4543 | -19.1692 | -65.9808 | 49.9736 | -19.0318 | -65.5078 | 48.5057 | -90.1392 | -87.3237
1710 | 0.1425 | 68.0537 | 1.2655 | 0.68196 | 0.017692 | 67.3717 | -8262.7952 | -21.0297 | -64.7229 | 49.9699 | -20.819 | -64.0743 | 48.5097 | -90.1378 | -87.3255
1711 | 0.14258 | 67.332 | 1.2832 | 0.92555 | 0.016724 | 66.4065 | -9055.0067 | -22.8079 | -63.3514 | 49.9662 | -22.4944 | -62.4806 | 48.5157 | -90.1363 | -87.3284
1712 | 0.14267 | 66.5447 | 1.2999 | 1.2306 | 0.015688 | 65.3141 | -9838.3071 | -24.4968 | -61.8717 | 49.9626 | -24.0437 | -60.7275 | 48.5239 | -90.1347 | -87.3328
1713 | 0.14275 | 65.6926 | 1.3156 | 1.6023 | 0.014597 | 64.0903 | -10611.9232 | -26.0897 | -60.2897 | 49.959 | -25.4533 | -58.8192 | 48.5343 | -90.1329 | -87.3388
1714 | 0.14283 | 64.7764 | 1.3302 | 2.0425 | 0.013469 | 62.7339 | -11375.0915 | -27.5804 | -58.6114 | 49.9555 | -26.7108 | -56.7633 | 48.5469 | -90.131 | -87.3466
1715 | 0.14292 | 63.797 | 1.3437 | 2.5493 | 0.012325 | 61.2478 | -12127.0588 | -28.9633 | -56.8436 | 49.9521 | -27.8059 | -54.5722 | 48.5616 | -90.129 | -87.3565
1716 | 0.143 | 62.7555 | 1.356 | 3.1164 | 0.01119 | 59.6391 | -12867.083 | -30.2327 | -54.9931 | 49.9487 | -28.7314 | -52.2621 | 48.5781 | -90.1269 | -87.3684
1717 | 0.14308 | 61.6529 | 1.3672 | 3.734 | 0.010082 | 57.9189 | -13594.4336 | -31.3839 | -53.0672 | 49.9454 | -29.4831 | -49.8532 | 48.5961 | -90.1247 | -87.3823
1718 | 0.14317 | 60.4902 | 1.3773 | 4.3891 | 0.0090198 | 56.1011 | -14308.3928 | -32.4123 | -51.0735 | 49.9421 | -30.0604 | -47.3677 | 48.6153 | -90.1223 | -87.3981
1719 | 0.14325 | 59.2685 | 1.3863 | 5.0669 | 0.0080136 | 54.2016 | -15008.2559 | -33.3139 | -49.0199 | 49.939 | -30.4658 | -44.8291 | 48.6353 | -90.1199 | -87.4158
1720 | 0.14333 | 57.9892 | 1.3943 | 5.752 | 0.0070703 | 52.2372 | -15693.3322 | -34.0852 | -46.9143 | 49.9359 | -30.7043 | -42.2608 | 48.6559 | -90.1173 | -87.4351
1721 | 0.14342 | 56.6534 | 1.4014 | 6.429 | 0.0061921 | 50.2244 | -16362.9455 | -34.7233 | -44.765 | 49.9329 | -30.7829 | -39.6851 | 48.6766 | -90.1146 | -87.4559
1722 | 0.1435 | 55.2625 | 1.4076 | 7.0838 | 0.0053779 | 48.1787 | -17016.435 | -35.2256 | -42.5805 | 49.93 | -30.7103 | -37.1223 | 48.6974 | -90.1119 | -87.478
1723 | 0.14358 | 53.8178 | 1.413 | 7.7037 | 0.0046243 | 46.1141 | -17653.1556 | -35.5904 | -40.3693 | 49.9271 | -30.4958 | -34.5907 | 48.7178 | -90.109 | -87.5011
1724 | 0.14367 | 52.3208 | 1.4176 | 8.2779 | 0.0039266 | 44.0429 | -18272.4789 | -35.816 | -38.1402 | 49.9244 | -30.1495 | -32.1059 | 48.7377 | -90.106 | -87.5251
1725 | 0.14375 | 50.7729 | 1.4215 | 8.7972 | 0.0032793 | 41.9757 | -18873.7937 | -35.9019 | -35.9019 | 49.9217 | -29.6813 | -29.6813 | 48.757 | -90.103 | -87.5498
1726 | 0.14383 | 49.1757 | 1.4248 | 9.2547 | 0.0026764 | 39.921 | -19456.5065 | -35.8475 | -33.6631 | 49.9191 | -29.1011 | -27.3278 | 48.7755 | -90.0999 | -87.5749
1727 | 0.14392 | 47.5307 | 1.4275 | 9.6448 | 0.0021122 | 37.8859 | -20020.0421 | -35.6533 | -31.4326 | 49.9166 | -28.4186 | -25.0544 | 48.793 | -90.0966 | -87.6004
1728 | 0.144 | 45.8395 | 1.4296 | 9.9637 | 0.0015812 | 35.8759 | -20563.8444 | -35.32 | -29.2192 | 49.9143 | -27.6428 | -22.8681 | 48.8096 | -90.0934 | -87.6261
1729 | 0.14408 | 44.1039 | 1.4312 | 10.209 | 0.0010781 | 33.895 | -21087.3766 | -34.8489 | -27.0316 | 49.912 | -26.7823 | -20.7745 | 48.8252 | -90.09 | -87.6517
1730 | 0.14417 | 42.3256 | 1.4322 | 10.3795 | 0.00059798 | 31.9461 | -21590.1219 | -34.2421 | -24.8783 | 49.9098 | -25.8449 | -18.7774 | 48.8397 | -90.0865 | -87.6772
1731 | 0.14425 | 40.5062 | 1.4328 | 10.4752 | 0.00013626 | 30.0309 | -22071.5843 | -33.5019 | -22.7678 | 49.9077 | -24.838 | -16.8799 | 48.8531 | -90.083 | -87.7025
1732 | 0.14433 | 38.6476 | 1.433 | 10.4972 | -0.00031135 | 28.1504 | -22531.2884 | -32.6312 | -20.7084 | 49.9057 | -23.7682 | -15.0837 | 48.8654 | -90.0794 | -87.7274
1733 | 0.14442 | 36.7516 | 1.4327 | 10.4471 | -0.0007489 | 26.3045 | -22968.7805 | -31.6336 | -18.7081 | 49.9038 | -22.6414 | -13.3901 | 48.8766 | -90.0758 | -87.7518
1734 | 0.1445 | 34.8201 | 1.4319 | 10.3276 | -0.0011802 | 24.4924 | -23383.6289 | -30.5131 | -16.7747 | 49.9021 | -21.4629 | -11.7993 | 48.8868 | -90.0721 | -87.7757
1735 | 0.14458 | 32.8549 | 1.4307 | 10.142 | -0.0016089 | 22.713 | -23775.424 | -29.274 | -14.9158 | 49.9004 | -20.2374 | -10.3115 | 48.8959 | -90.0684 | -87.7989
1736 | 0.14467 | 30.8581 | 1.4291 | 9.894 | -0.0020386 | 20.9641 | -24143.7792 | -27.9213 | -13.1388 | 49.8988 | -18.9689 | -8.9261 | 48.9041 | -90.0646 | -87.8213
1737 | 0.14475 | 28.8316 | 1.4271 | 9.5881 | -0.0024727 | 19.2435 | -24488.3308 | -26.4604 | -11.4504 | 49.8974 | -17.6608 | -7.6425 | 48.9112 | -90.0607 | -87.843
1738 | 0.14483 | 26.7774 | 1.4246 | 9.2292 | -0.0029147 | 17.5482 | -24808.7387 | -24.897 | -9.8574 | 49.896 | -16.3159 | -6.4599 | 48.9175 | -90.0569 | -87.8637
1739 | 0.14492 | 24.6975 | 1.4217 | 8.8226 | -0.0033678 | 15.8749 | -25104.6868 | -23.2374 | -8.366 | 49.8948 | -14.9364 | -5.3774 | 48.9229 | -90.0529 | -87.8835
1740 | 0.145 | 22.594 | 1.4183 | 8.3741 | -0.0038356 | 14.2199 | -25375.8828 | -21.4882 | -6.9819 | 49.8937 | -13.524 | -4.3942 | 48.9275 | -90.049 | -87.9023
1741 | 0.14508 | 20.4689 | 1.4145 | 7.8898 | -0.0043213 | 12.5792 | -25622.0591 | -19.6562 | -5.7106 | 49.8927 | -12.0797 | -3.5095 | 48.9313 | -90.045 | -87.9201
1742 | 0.14517 | 18.3244 | 1.4102 | 7.3762 | -0.0048282 | 10.9482 | -25842.9727 | -17.7487 | -4.5571 | 49.8918 | -10.6042 | -2.7227 | 48.9344 | -90.041 | -87.9367
1743 | 0.14525 | 16.1625 | 1.4054 | 6.8401 | -0.0053595 | 9.3224 | -26038.4054 | -15.7732 | -3.5257 | 49.891 | -9.0979 | -2.0336 | 48.9368 | -90.037 | -87.9522
1744 | 0.14533 | 13.9853 | 1.4 | 6.2886 | -0.0059183 | 7.6967 | -26208.1645 | -13.7376 | -2.6206 | 49.8903 | -7.5604 | -1.4422 | 48.9387 | -90.033 | -87.9665
1745 | 0.14542 | 11.7951 | 1.3941 | 5.729 | -0.0065071 | 6.0661 | -26352.0821 | -11.6499 | -1.8452 | 49.8898 | -5.9915 | -0.94895 | 48.9401 | -90.0289 | -87.9796
1746 | 0.1455 | 9.594 | 1.3876 | 5.1687 | -0.0071282 | 4.4254 | -26470.0164 | -9.5184 | -1.2025 | 49.8893 | -4.3905 | -0.55465 | 48.941 | -90.0249 | -87.9914
1747 | 0.14558 | 7.3842 | 1.3804 | 4.615 | -0.007783 | 2.7692 | -26561.8508 | -7.3514 | -0.69492 | 49.889 | -2.757 | -0.26061 | 48.9415 | -90.0208 | -88.002
1748 | 0.14567 | 5.1678 | 1.3727 | 4.0752 | -0.0084721 | 1.0926 | -26627.4946 | -5.1576 | -0.32449 | 49.8888 | -1.0905 | -0.068606 | 48.9418 | -90.0167 | -88.0113
1749 | 0.14575 | 2.947 | 1.3642 | 3.5563 | -0.0091948 | -0.60924 | -26666.8831 | -2.9456 | -0.092568 | 49.8886 | 0.60894 | 0.019137 | 48.9417 | -90.0127 | -88.0193
1750 | 0.14583 | 0.72405 | 1.355 | 3.0646 | -0.009949 | -2.3406 | -26679.9772 | -0.72405 | -7.9826e-15 | 49.8886 | 2.3406 | 2.5805e-14 | 48.9415 | -90.0086 | -88.026
1751 | 0.14592 | -1.4989 | 1.345 | 2.6059 | -0.010731 | -4.1049 | -26666.764 | 1.4982 | -0.047082 | 49.8888 | 4.1028 | -0.12894 | 48.9412 | -90.0046 | -88.0315
1752 | 0.146 | -3.7197 | 1.3343 | 2.1849 | -0.011535 | -5.9046 | -26627.2564 | 3.7123 | -0.23356 | 49.889 | 5.8929 | -0.37075 | 48.9409 | -90.0006 | -88.0357
1753 | 0.14608 | -5.9361 | 1.3228 | 1.805 | -0.012355 | -7.741 | -26561.4935 | 5.9097 | -0.55863 | 49.8893 | 7.7067 | -0.7285 | 48.9405 | -89.9966 | -88.0388
1754 | 0.14617 | -8.1459 | 1.3104 | 1.4683 | -0.013183 | -9.6141 | -26469.54 | 8.0816 | -1.0209 | 49.8897 | 9.5383 | -1.205 | 48.9403 | -89.9926 | -88.0408
1755 | 0.14625 | -10.3469 | 1.2972 | 1.1754 | -0.014009 | -11.5224 | -26351.4866 | 10.2195 | -1.6186 | 49.8903 | 11.3805 | -1.8025 | 48.9401 | -89.9887 | -88.0418
1756 | 0.14633 | -12.5371 | 1.2832 | 0.92568 | -0.014826 | -13.4627 | -26207.4498 | 12.315 | -2.3492 | 49.8909 | 13.2243 | -2.5227 | 48.9401 | -89.9848 | -88.042
1757 | 0.14642 | -14.7141 | 1.2684 | 0.71686 | -0.015624 | -15.431 | -26037.5717 | 14.3598 | -3.2098 | 49.8917 | 15.0593 | -3.3662 | 48.9402 | -89.9809 | -88.0413
1758 | 0.1465 | -16.8759 | 1.2528 | 0.54577 | -0.016398 | -17.4217 | -25842.0198 | 16.3458 | -4.1969 | 49.8926 | 16.8744 | -4.3326 | 48.9405 | -89.977 | -88.04
1759 | 0.14658 | -19.0204 | 1.2364 | 0.40843 | -0.017142 | -19.4288 | -25620.9871 | 18.2652 | -5.3065 | 49.8935 | 18.6574 | -5.4205 | 48.9411 | -89.9733 | -88.0382
1760 | 0.14667 | -21.1454 | 1.2192 | 0.30042 | -0.017853 | -21.4458 | -25374.6917 | 20.1105 | -6.5343 | 49.8946 | 20.3962 | -6.6271 | 48.9418 | -89.9695 | -88.0359
1761 | 0.14675 | -23.2488 | 1.2014 | 0.21716 | -0.018529 | -23.466 | -25103.3765 | 21.8744 | -7.8753 | 49.8957 | 22.0787 | -7.9488 | 48.9427 | -89.9658 | -88.0333
1762 | 0.14683 | -25.3286 | 1.1829 | 0.15427 | -0.01917 | -25.4829 | -24807.3093 | 23.55 | -9.3241 | 49.897 | 23.6934 | -9.3809 | 48.9437 | -89.9622 | -88.0304
1763 | 0.14692 | -27.3827 | 1.1637 | 0.10769 | -0.019775 | -27.4904 | -24486.7821 | 25.1306 | -10.875 | 49.8983 | 25.2294 | -10.9178 | 48.9449 | -89.9586 | -88.0274
1764 | 0.147 | -29.4091 | 1.1439 | 0.073859 | -0.020347 | -29.4829 | -24142.1114 | 26.6101 | -12.5218 | 49.8998 | 26.677 | -12.5532 | 48.9463 | -89.9551 | -88.0242
1765 | 0.14708 | -31.4057 | 1.1236 | 0.049765 | -0.020887 | -31.4555 | -23773.637 | 27.9827 | -14.2579 | 49.9013 | 28.027 | -14.2805 | 48.9478 | -89.9516 | -88.021
1766 | 0.14717 | -33.3707 | 1.1027 | 0.032933 | -0.021397 | -33.4036 | -23381.7227 | 29.243 | -16.0765 | 49.903 | 29.2718 | -16.0923 | 48.9495 | -89.9482 | -88.0178
1767 | 0.14725 | -35.302 | 1.0813 | 0.0214 | -0.021877 | -35.3234 | -22966.7551 | 30.386 | -17.9702 | 49.9047 | 30.4044 | -17.9811 | 48.9512 | -89.9449 | -88.0146
1768 | 0.14733 | -37.1979 | 1.0594 | 0.013649 | -0.02233 | -37.2115 | -22529.1438 | 31.4072 | -19.9316 | 49.9065 | 31.4187 | -19.9389 | 48.9531 | -89.9416 | -88.0115
1769 | 0.14742 | -39.0563 | 1.0371 | 0.0085421 | -0.022757 | -39.0648 | -22069.3204 | 32.3027 | -21.9529 | 49.9084 | 32.3098 | -21.9577 | 48.955 | -89.9384 | -88.0083
1770 | 0.1475 | -40.8755 | 1.0143 | 0.0052429 | -0.023157 | -40.8807 | -21587.7388 | 33.069 | -24.026 | 49.9103 | 33.0732 | -24.0291 | 48.9571 | -89.9353 | -88.0053
1771 | 0.14758 | -42.6536 | 0.99116 | 0.0031544 | -0.023532 | -42.6568 | -21084.8742 | 33.703 | -26.1427 | 49.9124 | 33.7055 | -26.1447 | 48.9592 | -89.9323 | -88.0023
1772 | 0.14767 | -44.389 | 0.96763 | 0.0018593 | -0.023882 | -44.3909 | -20561.2227 | 34.2023 | -28.2946 | 49.9145 | 34.2038 | -28.2958 | 48.9614 | -89.9294 | -87.9994
1773 | 0.14775 | -46.08 | 0.94375 | 0.0010729 | -0.024207 | -46.081 | -20017.3011 | 34.5651 | -30.4732 | 49.9167 | 34.5659 | -30.4739 | 48.9637 | -89.9265 | -87.9966
1774 | 0.14783 | -47.7247 | 0.91954 | 0.00060577 | -0.024507 | -47.7253 | -19453.6462 | 34.7898 | -32.6698 | 49.919 | 34.7903 | -32.6702 | 48.966 | -89.9237 | -87.9939
1775 | 0.14792 | -49.3217 | 0.89503 | 0.00033436 | -0.024782 | -49.322 | -18870.814 | 34.8757 | -34.8757 | 49.9213 | 34.8759 | -34.8759 | 48.9684 | -89.9211 | -87.9912
1776 | 0.148 | -50.8693 | 0.87025 | 0.00018027 | -0.025033 | -50.8695 | -18269.3799 | 34.8225 | -37.0821 | 49.9237 | 34.8226 | -37.0823 | 48.9709 | -89.9185 | -87.9887
1777 | 0.14808 | -52.3661 | 0.84522 | 9.4856e-05 | -0.025258 | -52.3662 | -17649.9371 | 34.6303 | -39.2804 | 49.9262 | 34.6304 | -39.2805 | 48.9734 | -89.916 | -87.9863
1778 | 0.14817 | -53.8105 | 0.81996 | 4.8662e-05 | -0.025458 | -53.8106 | -17013.0971 | 34.3001 | -41.4617 | 49.9287 | 34.3001 | -41.4617 | 48.976 | -89.9136 | -87.9839
1779 | 0.14825 | -55.2011 | 0.7945 | 2.4313e-05 | -0.025633 | -55.2012 | -16359.4882 | 33.8332 | -43.6175 | 49.9313 | 33.8332 | -43.6175 | 48.9787 | -89.9113 | -87.9817
1780 | 0.14833 | -56.5366 | 0.76887 | 1.1817e-05 | -0.025782 | -56.5366 | -15689.7555 | 33.2314 | -45.7391 | 49.9339 | 33.2314 | -45.7391 | 48.9814 | -89.9091 | -87.9796
1781 | 0.14842 | -57.8157 | 0.74309 | 5.5799e-06 | -0.025905 | -57.8157 | -15004.5597 | 32.4972 | -47.8182 | 49.9366 | 32.4972 | -47.8182 | 48.9841 | -89.907 | -87.9775
1782 | 0.1485 | -59.037 | 0.71718 | 2.5562e-06 | -0.026003 | -59.037 | -14304.5771 | 31.6336 | -49.8466 | 49.9394 | 31.6336 | -49.8466 | 48.9869 | -89.9051 | -87.9756
1783 | 0.14858 | -60.1994 | 0.69118 | 1.1343e-06 | -0.026075 | -60.1994 | -13590.4984 | 30.644 | -51.8161 | 49.9421 | 30.644 | -51.8161 | 48.9897 | -89.9032 | -87.9738
1784 | 0.14867 | -61.3017 | 0.6651 | 4.8677e-07 | -0.026121 | -61.3017 | -12863.0282 | 29.5323 | -53.7191 | 49.945 | 29.5323 | -53.7191 | 48.9926 | -89.9014 | -87.9721
1785 | 0.14875 | -62.3429 | 0.63898 | 2.0161e-07 | -0.02614 | -62.3429 | -12122.8844 | 28.3031 | -55.5479 | 49.9478 | 28.3031 | -55.5479 | 48.9955 | -89.8997 | -87.9705
1786 | 0.14883 | -63.3218 | 0.61284 | 8.0432e-08 | -0.026134 | -63.3218 | -11370.7975 | 26.9611 | -57.2953 | 49.9507 | 26.9611 | -57.2953 | 48.9985 | -89.8982 | -87.9691
1787 | 0.14892 | -64.2377 | 0.58671 | 3.0835e-08 | -0.026102 | -64.2377 | -10607.5095 | 25.5119 | -58.9544 | 49.9537 | 25.5119 | -58.9544 | 49.0015 | -89.8967 | -87.9677
1788 | 0.149 | -65.0895 | 0.56061 | 1.133e-08 | -0.026044 | -65.0895 | -9833.7737 | 23.961 | -60.5187 | 49.9566 | 23.961 | -60.5187 | 49.0045 | -89.8954 | -87.9665
1789 | 0.14908 | -65.8764 | 0.53456 | 3.9785e-09 | -0.02596 | -65.8764 | -9050.3537 | 22.3148 | -61.9818 | 49.9596 | 22.3148 | -61.9818 | 49.0075 | -89.8941 | -87.9653
1790 | 0.14917 | -66.5976 | 0.5086 | 1.3307e-09 | -0.02585 | -66.5976 | -8258.0224 | 20.5798 | -63.3381 | 49.9627 | 20.5798 | -63.3381 | 49.0105 | -89.893 | -87.9643
1791 | 0.14925 | -67.2525 | 0.48275 | 4.2236e-10 | -0.025714 | -67.2525 | -7457.5618 | 18.7628 | -64.5821 | 49.9657 | 18.7628 | -64.5821 | 49.0136 | -89.892 | -87.9634
1792 | 0.14933 | -67.8403 | 0.45704 | 1.2668e-10 | -0.025553 | -67.8403 | -6649.7618 | 16.8712 | -65.709 | 49.9688 | 16.8712 | -65.709 | 49.0167 | -89.8911 | -87.9626
1793 | 0.14942 | -68.3606 | 0.43148 | 3.5726e-11 | -0.025367 | -68.3606 | -5835.4195 | 14.9124 | -66.7143 | 49.9718 | 14.9124 | -66.7143 | 49.0198 | -89.8903 | -87.9619
1794 | 0.1495 | -68.8128 | 0.40612 | 9.421e-12 | -0.025155 | -68.8128 | -5015.3386 | 12.8942 | -67.5939 | 49.9749 | 12.8942 | -67.5939 | 49.0229 | -89.8897 | -87.9614
1795 | 0.14958 | -69.1964 | 0.38096 | 2.3077e-12 | -0.024918 | -69.1964 | -4190.3283 | 10.8247 | -68.3444 | 49.978 | 10.8247 | -68.3444 | 49.026 | -89.8891 | -87.9609
1796 | 0.14967 | -69.511 | 0.35604 | 5.2102e-13 | -0.024656 | -69.511 | -3361.2028 | 8.712 | -68.9629 | 49.9811 | 8.712 | -68.9629 | 49.0291 | -89.8887 | -87.9606
1797 | 0.14975 | -69.7565 | 0.33139 | 1.0744e-13 | -0.02437 | -69.7565 | -2528.7802 | 6.5647 | -69.4469 | 49.9842 | 6.5647 | -69.4469 | 49.0322 | -89.8884 | -87.9604
1798 | 0.14983 | -69.9324 | 0.30702 | 2.0016e-14 | -0.02406 | -69.9324 | -1693.8819 | 4.3911 | -69.7944 | 49.9873 | 4.3911 | -69.7944 | 49.0353 | -89.8881 | -87.9603
1799 | 0.14992 | -70.0387 | 0.28296 | 3.324e-15 | -0.023725 | -70.0387 | -857.332 | 2.2 | -70.0042 | 49.9904 | 2.2 | -70.0042 | 49.0384 | -89.888 | -87.9603
1800 | 0.15 | -70.0753 | 0.25923 | 4.8412e-16 | -0.023367 | -70.0753 | -19.9558 | 6.5239e-13 | -70.0753 | 49.9935 | 6.5239e-13 | -70.0753 | 49.0415 | -89.888 | -87.9604
CT Saturation Calculator
VERSION:
30 Dec 2002

## Sheet2
MODIFICATION HISTORY
3 Oct '00: Added strict calculation of RP and hence A; added CT model on sheet 4.
22 Dec '00: Corrected Vs notation, expanded time frame, exposed calculations.
5 Jan '01: Added diagram below plot.
18 Jan '01: Deleted figures on Sheet 4.
26 Feb '01: Clarified INSTRUCTIONS wording.
4 Jun '01: Changed notation: 'form factor FF' to 'RP'
5 Mar '02: Remanent flux is now 'locked,' for all t<0. Otherwise, incorrect results for low X/R.
17 Sep '02: Cell for X/R ratio was inadvertantly locked. Now unlocked.
26 Sep '02: "HOW TO MEASURE SLOPE" diagram added.
4 Oct '02: Added "rms of fundamental" to calculations and plot.
30 Dec 02: Improved asterisk note on error current, and added phasor diagram.
INSTRUCTIONS
1. Determine the saturation voltage (Vs) for the CT in question. This is defined as the rms excitation voltage corresponding to ten-per-cent error current. For example, for a nominal five-amp CT which is expected to handle 100 amps with a ten per cent error, the error current at the saturation voltage Vs, is ten amps.* For maximum accuracy, this should be a measured value supplied by the manufacturer. For example, a C400 CT has a nominal Vs of 400 volts rms, but the actual measured Vs will be a higher value; it could be 420 volts rms for example.
Incidentally, the actual measurements by the manufacturer may not have been made with a "true rms" meter. It has been determined that the error due to use of a "rectified average" type meter, for example, is not significant.
2. Determine the slope (1/S) of the upper part of the saturation curve, being careful that the curve is plotted on log-log scales with the decade spacing equal on both axes. "S" is defined as the reciprocal of this slope. You should get a slope such that S is in the neighborhood of 15<S<25. Note that the result is not very sensitive to the value of S.
SEE THE DIAGRAM TO THE RIGHT >>>>>>>>>>>>>>>>>
3. Enter other parameters such as the CT winding resistance, the burden, the degree of dc-offset in the primary current waveform (up to 1 per unit), the primary system X/R ratio, the remanence**, and the primary symmetrical rms current.
Once any change to an INPUT parameter is made, a new plot appears automatically. The scale adjustment is automatic and the plot is believed to be self-explanatory.
_______
*This is a definition used in the Guide that is not strictly correct but is used here to be consistent with the Guide. If the ideal (maximum rated) secondary current is 100 amps rms and the exciting (error) current is 10 amps rms, then the actual secondary current is typically 99+ amps rms, not 90 amps rms. This is because the exciting current is both out of phase and non-sinusoidal, so simple subtraction does not apply. So when we specify 10 amps error current at 100 amps secondary current, the error is actually less than 1% typically, but includes a phase error of, say 5 degrees, leading.
**Note that the per unit remanence is defined relative to Vs. If the knee-point voltage (45 degree slope point) is 80% of Vs, then the maximum remanence value is 0.8. Note that the polarities for this simulation are such that a positive remanence is the "worst-case" condition for premature saturation.

## Sheet4
BACKGROUND
This program is intended to show LARGE CURRENT or HIGH BURDEN behavior only; it does not accurately represent the conditions
at the low end portion of the iron saturation curve. Consequently, hysteresis loss and eddy current loss are not modeled because
they have negligible effect on the saturation region behavior.
Another assumption is that the usual log-log plot of rms voltage versus rms current for the saturation curve is correct when plotted
as a straight line for the saturated portion of the curve. This implies a pure power law relating instantaneous voltage to
instantaneous current, and the slope of the upper portion of the commonly-used log-log plot is in the neighborhood of 1/20 for a
modern toroidal CT. The value for Vs, the "saturation voltage," is assumed to be at a properly measured rms value of 10 amps
excitation current, the voltage being sinusoidal and the current being related to flux by an Sth(only) order function. If the 10-amp
value is measureed using a 'not-true-rms' meter, the error is not great enough to cause significant error.
The program has been checked against a variety of examples, including those of the recent IEEE paper "Mathematical Models for
Current, Voltage, and Coupling Capacitor Voltage Transformers," Working Group C5 of PSRC, IEEE Trans on Power Delivery, Jan
2000, pp. 62-72. (Note that there is an error in figures 4a and 5a of that paper: there was actually non-zero remanence for this
case, as confirmed with the authors.)