## Instructions
IEEE PSRC WG D22
COMTRADE Calculator for Varying Frequency and Voltage Version 2.0 2012.04.20
This COMTRADE Calculator creates transient files for the purpose of testing the performance of distance relays during conditions when the system frequency and are varying. there are test cases prescribed by Working Group D22.The files are saved in COMTRADE format and can be imported into any relay test system that accept this file format.
Instructions for Use:
For typical use, simply select the relay characteristic type, enter or change the settings and nominal values in the light yellow colored cells. You may opt to check or uncheck the box "Keep Z test point constant with V ramp"; checking it will ramp the current when the voltage ramps, otherwise current will remain constant. Select the test case from the dropdown box, and click on the Create COMTRADE File button. It will then prompt you to save the file. Select another test case, click the button and save the new file.
Custom test cases can be done. Some of the cells are color coded to guide you in making changes and to understand the behavior of the tool when these changes are made. Note that changes that you have made in light geen boxes will be replaced with default values if the test case is other than "Custom" when you check on uncheck the "Keep Z test point constant" checkbox.
Cell Color | Description
Light Yellow | These are cells that you would normally change, and they include relay setting parameters
Light Olive Green | These are the suggested filenames and test description that change when you select a PSRC WG D22 test case. You can change them for a particular test case but they will change again when the test case selection is changed.
Light Green | These cells are automatically changed when a new test case is selected. You can change them for a particular case and create the COMTRADE file. Be aware that selecting another case will again change them to new values according to the new selection.
Red | These are default values that are used in some light green cells with similar names.
Gray | These cells contain formulas and are locked and cannot be changed unless sheet protection is turned off.
Back to Calculator
Note about MS Excel security restrictions:
This tool contains macros and may not run depending on the security settings that have been set in MS Excel. This tool can be used in MS Excel versions 2000 through 2010. The procedure of allowing macros to run in Excel is different from one version to another. Consult the Excel help file for the procedure to allow macros to run.

## WGD22
| COMTRADE Calculator for Varying Frequency and Voltage Version 2.0 2012.04.20 | [6 empty] | Read Instructions
| PSRC WG D22 Test Case | Case 34 |  | Header/Description: |  | Sec_V10085100_F605660_dfdt2 file tests relay security for varying frequency. Inital voltage at 1 pu and nominal frequency. Freq. ramps to 56Hz at -2Hz/s, then back to init. freq. at 1Hz/s. Voltage ramps to 0.85 pu, then back to 1 pu.
| Suggested File Name | Sec_V10085100_F605660_dfdt2
| Station Name | IEEE PSRC WG D22
| Circuit Name | Line 1
| Sampling Rate | 10000 | /s | [5 empty] | ToDo: graph delta angle of VA vs Vref
Graph Points
| Nominal Voltage, Vn PhPh | 120 | V | [8 empty] | V | f
| Nominal Current, In | 5 | A | [7 empty] | -0.2 | 1 | 60
| Nominal Frequency, fn | 60 | Hz | [7 empty] | -0.1 | 1 | 60
| Characteristic Type | Mho | [8 empty] | 0 | 1 | 60
| Impedance Z Reach | 30 | Ω | [7 empty] | 0.1 | 1 | 60
| Characteristic Angle | 80 | ° | [6 empty] | 0.0125 | 0.1125 | 0.99988 | 59.9969
| Quad Resistive Reach, per ph. | 20 | Ω | [6 empty] | 0.025 | 0.125 | 0.99953 | 59.9875
| Load Angle | 35 | ° | [6 empty] | 0.0375 | 0.1375 | 0.99895 | 59.9719
| Z Margin @ Load Angle | 10 | % | [6 empty] | 0.05 | 0.15 | 0.99813 | 59.95
| Z Test Point | 23.3345 | Ω | [7 empty] | 2.125 | 0.85 | 56 |  | 1.975
|  | TRUE | [8 empty] | 2.125 | 0.85 | 56
| Stabilize relay @ Vn, fn and I=0 | [9 empty] | 6.125 | 1 | 60
| Stabilization duration | 0.1 | s | [7 empty] | 6.125 | 1 | 60 |  | -2
| Ramp duration to Point 0 | 0.1 | s
| Point 0: Initial conditions before frequency ramp |  |  |  | Point 1: Vary V and f |  |  |  | Point 2: Vary V and f back in direction of initial Point 0
| Z Test Point | 23.3345 | Ω |  | Frequency | 56 | Hz |  | Frequency | 60 | Hz
| Z angle | 35 | ° |  | V amplitude, pu | 0.85 | pu |  | V amplitude, pu | 1 | pu
| Frequency | 60 | Hz |  | V amplitude, PhN | 58.8897 | V |  | V amplitude, PhN | 69.282 | V
| VA initial amplitude | 1 | pu |  | V ph.angle | 0 | ° |  | V ph.angle | 0 | °
| VA amplitude, PhN | 69.282 | V |  | I amplitude | 2.5237 | A |  | I amplitude | 2.9691 | A
| VA ph.angle | 0 | ° |  | I ph.angle | -35 | ° |  | I ph.angle | -35 | °
| V for I calculation | 1 | pu |  | df/dt | -2 | Hz/s |  | df/dt | 1 | Hz/s
| IA amplitude | 2.9691 | A |  | dV/dt | -5.132 | V/s |  | dV/dt | 2.5981 | V/s
| IA ph.angle | -35 | ° |  | dI/dt | -0.21993 | A/s |  | dI/dt | 0.11134 | A/s
| Duration of initial condition | 0.1 | s |  | Ramp1 duration | 2.025 | s |  | Ramp2 duration | 4 | s
[5 empty] | Additonal time at Ramp1 end | 0 | s |  | Additonal time at Ramp2 end | 0 | s
| Default WGD22 Dur.of Init.Cond. | 0.1 | s |  | Default addl time, Ramp1 end | 0 | s |  | Default addl time, Ramp2 end | 0 | s
| Default WGD22 Z margin | 10 | % |  | Initial ramp (quadratic) duration | 0.05 | s
|  | stabilize | Vramp0 | dur. 0 | Ramp 3-4 | addl time | Ramp5-6 | add'l time
NoOfSources | 8
| SourceNumber | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | [8 empty] | mtaRadians | 1.3963 |  | Circle Points
| SourceNames | VA | VB | VC | IA | IB | IC | VAref | IAref | [8 empty] | mhoRadius | 15 |  | Angle | R | X
| SourceUnit | [16 empty] | mhoCenterR | 2.6047 |  | 0 | 17.6047 | 14.7721 | bar: 1 to 8
[18 empty] | mhoCenterX | 14.7721 |  | 5 | 17.5476 | 16.0795
NoOfStatesRamps | 7 | State1 | State2 | State3 | State4 | State5 | State6 | State7 |  |  | Equation: y = Qinit + a t2 | V | f | [7 empty] | 10 | 17.3768 | 17.3768
Duration | tStateRamp | 0.1 | 0.1 | 0.1 | 2 | 0 | 4 | 0 |  |  | Ramp1 Rate, dV(pu)/dt & df/dt | -0.075 | -2 |  |  |  |  | Load Point |  |  | 15 | 17.0936 | 18.6544
[11 empty] | Coeficients, aV & aF | -0.75 | -20 |  |  |  |  | Zload | 23.3345 |  | 20 | 16.7001 | 19.9024
| VA | State1 | State2 | State3 | State4 | State5 | State6 | State7 |  |  | Value at end of quad curve ramp | 0.99813 | 59.95 |  |  |  |  | Angle | 35 |  | 25 | 16.1993 | 21.1114
| MagFrom1 | 69.282 | 69.282 | 69.282 | 69.282 | 58.8897 | 58.8897 | 69.282 |  |  | Remaining time to end of straight ramp | - | 1.975 | s |  |  |  | R | X |  | 30 | 15.5951 | 22.2721
| MagTo1 | 69.282 | 69.282 | 69.282 | 58.8897 | 58.8897 | 69.282 | 69.282 |  |  | Total ramp1 time | - | 2.025 | s |  |  |  | 0 | 0 |  | 35 | 14.892 | 23.3758
| AngFrom1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | LoadR | LoadX | 19.1145 | 13.3841 |  | 40 | 14.0954 | 24.4139
| AngTo1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Note: When calculating in VBA | [10 empty] | 45 | 13.2113 | 25.3787
| FreqFrom1 | 60 | 60 | 60 | 60 | 56 | 56 | 60 | [12 empty] | 50 | 12.2465 | 26.2628
| FreqTo1 | 60 | 60 | 60 | 56 | 56 | 60 | 60 | [9 empty] | TableCharType |  |  | 55 | 11.2084 | 27.0594
| TimeConst1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | Mho |  |  | 60 | 10.1047 | 27.7625
| dq/dt | 0 | 0 | 0 | -5.1962 | #DIV/0! | 2.5981 | #DIV/0! | [9 empty] | Quad |  |  | 65 | 8.944 | 28.3667
| dPh/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [12 empty] | 70 | 7.735 | 28.8675
| df/dt | 0 | 0 | 0 | -2 | #DIV/0! | 1 | #DIV/0! | [12 empty] | 75 | 6.487 | 29.261
| VB | State1 | State2 | State3 | State4 | State5 | State6 | State7 | [8 empty] | Quad Calculations |  |  |  | 80 | 5.2094 | 29.5442
| MagFrom2 | 69.282 | 69.282 | 69.282 | 69.282 | 58.8897 | 58.8897 | 69.282 | [8 empty] | Rzreach | 0 |  |  | 85 | 3.9121 | 29.715
| MagTo2 | 69.282 | 69.282 | 69.282 | 58.8897 | 58.8897 | 69.282 | 69.282 | [8 empty] | Xzreach | 0 |  |  | 90 | 2.6047 | 29.7721
| AngFrom2 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | [8 empty] | Rset | 0 |  |  | 95 | 1.2974 | 29.715
| AngTo2 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | [8 empty] | Pt4mag | 0 |  |  | 100 | 0 | 29.5442
| FreqFrom2 | 60 | 60 | 60 | 60 | 56 | 56 | 60 | [8 empty] | Pt4ang | -10 |  |  | 105 | -1.2776 | 29.261
| FreqTo2 | 60 | 60 | 60 | 56 | 56 | 60 | 60 | [8 empty] | QuadPoints | R | X |  | 110 | -2.5256 | 28.8675
| TimeConst2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | Pt4 | 0 | 0 | Pt1Ang | 115 | -3.7346 | 28.3667 |  | Initial Voltage for 1.0 second |  |  |  | 0.85 pu | 0.90 pu | 0.95 pu | 1.0 pu | 1.00 pu |  | 0.85 pu | 0.90 pu | 0.95 pu | 1.0 pu | 1.00 pu
| dq/dt | 0 | 0 | 0 | -5.1962 | #DIV/0! | 2.5981 | #DIV/0! | [8 empty] | Pt1 | 0 | 0 | 0 | 120 | -4.8953 | 27.7625 |  | Lowest voltage |  |  |  | 0.85 pu | 0.90 pu | 0.95 pu | 1.0 pu | 0.85 pu |  | 0.85 pu | 0.90 pu | 0.95 pu | 1.0 pu | 0.85 pu
| dPh/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [8 empty] | Pt2 | 0 | 0 |  | 125 | -5.9989 | 27.0594 |  | Calculate Current for an angle |  |  |  | 0.85 pu | 0.90 pu | 0.95 pu | 1.0 pu | 0.85 pu |  | 0.85 pu | 0.90 pu | 0.95 pu | 1.0 pu | 0.85 pu
| df/dt | 0 | 0 | 0 | -2 | #DIV/0! | 1 | #DIV/0! | [8 empty] | Pt3 | 0 | 0 |  | 130 | -7.0371 | 26.2628 |  | or 30 deg for an impedance
| VC | State1 | State2 | State3 | State4 | State5 | State6 | State7 | [8 empty] | Pt4 | 0 | 0 |  | 135 | -8.0019 | 25.3787 |  | ??% outside/inside the relay's |  |  |  | 5 | 5 | 5 | 5 | 5 |  | -5 | -5 | -5 | -5 | -5
| MagFrom3 | 69.282 | 69.282 | 69.282 | 69.282 | 58.8897 | 58.8897 | 69.282 | [12 empty] | 140 | -8.8859 | 24.4139 |  | operating boundary
| MagTo1 | 69.282 | 69.282 | 69.282 | 58.8897 | 58.8897 | 69.282 | 69.282 | [8 empty] | MinQuadR | 0 |  |  | 145 | -9.6826 | 23.3758
| AngFrom3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | [8 empty] | MaxQuadR | 0 |  |  | 150 | -10.3857 | 22.2721 |  | Vary frequency from 60 Hz to 56 Hz |  |  |  | 1 Hz/s | 1 Hz/s | 1 Hz/s | 1 Hz/s | 1 Hz/s |  | 1 Hz/s | 1 Hz/s | 1 Hz/s | 1 Hz/s | 1 Hz/s
| AngTo3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | [8 empty] | MinQuadX | 0 |  |  | 155 | -10.9899 | 21.1114 |  | at specified rate and then return to |  |  |  | 2 Hz/s | 2 Hz/s | 2 Hz/s | 2 Hz/s | 2 Hz/s |  | 2 Hz/s | 2 Hz/s | 2 Hz/s | 2 Hz/s | 2 Hz/s
| FreqFrom3 | 60 | 60 | 60 | 60 | 56 | 56 | 60 | [8 empty] | MaxQuadX | 0 |  |  | 160 | -11.4907 | 19.9024 |  | 60 Hz at 1 Hz/s |  |  |  | 3 Hz/s | 3 Hz/s | 3 Hz/s | 3 Hz/s | 3 Hz/s |  | 3 Hz/s | 3 Hz/s | 3 Hz/s | 3 Hz/s | 3 Hz/s
| FreqTo3 | 60 | 60 | 60 | 56 | 56 | 60 | 60 | [12 empty] | 165 | -11.8842 | 18.6544 | [5 empty] | 4 Hz/s | 4 Hz/s | 4 Hz/s | 4 Hz/s | 4 Hz/s |  | 4 Hz/s | 4 Hz/s | 4 Hz/s | 4 Hz/s | 4 Hz/s
| TimeConst3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 170 | -12.1674 | 17.3768
| dq/dt | 0 | 0 | 0 | -5.1962 | #DIV/0! | 2.5981 | #DIV/0! | [12 empty] | 175 | -12.3382 | 16.0795 |  | Vary frequency from 60 Hz to 64 Hz |  |  |  | 1 Hz/s | 1 Hz/s | 1 Hz/s | 1 Hz/s | 1 Hz/s |  | 1 Hz/s | 1 Hz/s | 1 Hz/s | 1 Hz/s | 1 Hz/s
| dPh/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [12 empty] | 180 | -12.3953 | 14.7721 |  | at specified rate and then return to |  |  |  | 2 Hz/s | 2 Hz/s | 2 Hz/s | 2 Hz/s | 2 Hz/s |  | 2 Hz/s | 2 Hz/s | 2 Hz/s | 2 Hz/s | 2 Hz/s
| df/dt | 0 | 0 | 0 | -2 | #DIV/0! | 1 | #DIV/0! | [12 empty] | 185 | -12.3382 | 13.4648 |  | 60 Hz at 1 Hz/s |  |  |  | 3 Hz/s | 3 Hz/s | 3 Hz/s | 3 Hz/s | 3 Hz/s |  | 3 Hz/s | 3 Hz/s | 3 Hz/s | 3 Hz/s | 3 Hz/s
| IA | State1 | State2 | State3 | State4 | State5 | State6 | State7 | [12 empty] | 190 | -12.1674 | 12.1674 | [5 empty] | 4 Hz/s | 4 Hz/s | 4 Hz/s | 4 Hz/s | 4 Hz/s |  | 4 Hz/s | 4 Hz/s | 4 Hz/s | 4 Hz/s | 4 Hz/s
| MagFrom4 | 0 | 0 | 2.9691 | 2.9691 | 2.5237 | 2.5237 | 2.9691 | [12 empty] | 195 | -11.8842 | 10.8898 |  | Case 2
| MagTo4 | 0 | 2.9691 | 2.9691 | 2.5237 | 2.5237 | 2.9691 | 2.9691 | [12 empty] | 200 | -11.4907 | 9.6418 | Margin
| AngFrom4 | 325 | 325 | -35 | -35 | -35 | -35 | -35 | [12 empty] | 205 | -10.9899 | 8.4328 |  |  |  | Margin | Cal current at V | Initial V | Vary V down to | Bring back V to | Vary f to | at df/dt | Bring back freq to | at df/dt | Flat 1 | Flat2 | Flat 3
| AngTo4 | 325 | 325 | -35 | -35 | -35 | -35 | -35 | [12 empty] | 210 | -10.3857 | 7.2721 | Freq0=fn |  |  |  | VforIcalcPu | Vmag0pu | Vmag1pu | Vmag2pu | Freq1 | dfdt1 | Freq2 | dfdt2 | tState0 | t1AddlTime | t2AddlTime
| FreqFrom4 | 60 | 60 | 60 | 60 | 56 | 56 | 60 | [12 empty] | 215 | -9.6826 | 6.1685 | Vmag0pu |  | FileName |  | pu | pu | pu | pu | Hz | Hz/s | Hz | Hz/s | s | s | s
| FreqTo4 | 60 | 60 | 60 | 56 | 56 | 60 | 60 | [12 empty] | 220 | -8.8859 | 5.1303 | Vang0 | Custom | [14 empty] | HeaderInfo
| TimeConst4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 225 | -8.0019 | 4.1655 | tState0 | Case 1 | Sec_V100100100_F605660_dfdt1 | 10 | 1 | 1 | 1 | 1 | 56 | -1 | 60 | 1 | 0.1 | 0 | 0
| dq/dt | 0 | 29.6908 | 0 | -0.22268 | #DIV/0! | 0.11134 | #DIV/0! | [12 empty] | 230 | -7.0371 | 3.2814 |  | Case 2 | Sec_V100100100_F605660_dfdt2 | 10 | 1 | 1 | 1 | 1 | 56 | -2 | 60 | 1 | 0.1 | 0 | 0
| dPh/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [12 empty] | 235 | -5.9989 | 2.4848 | Freq1 | Case 3 | Sec_V100100100_F605660_dfdt4 | 10 | 1 | 1 | 1 | 1 | 56 | -4 | 60 | 1 | 0.1 | 0 | 0
| df/dt | 0 | 0 | 0 | -2 | #DIV/0! | 1 | #DIV/0! | [12 empty] | 240 | -4.8953 | 1.7817 | Vmag1pu | Case 4 | Sec_V100100100_F605660_dfdt8 | 10 | 1 | 1 | 1 | 1 | 56 | -8 | 60 | 1 | 0.1 | 0 | 0
| IB | State1 | State2 | State3 | State4 | State5 | State6 | State7 | [12 empty] | 245 | -3.7346 | 1.1775 | dfdt1 | Case 5 | Sec_V959595_F605660_dfdt1 | 10 | 0.95 | 0.95 | 0.95 | 0.95 | 56 | -1 | 60 | 1 | 0.1 | 0 | 0
| MagFrom5 | 0 | 0 | 2.9691 | 2.9691 | 2.5237 | 2.5237 | 2.9691 | [12 empty] | 250 | -2.5256 | 0.67673 | t1AddlTime | Case 6 | Sec_V959595_F605660_dfdt2 | 10 | 0.95 | 0.95 | 0.95 | 0.95 | 56 | -2 | 60 | 1 | 0.1 | 0 | 0
| MagTo5 | 0 | 2.9691 | 2.9691 | 2.5237 | 2.5237 | 2.9691 | 2.9691 | [12 empty] | 255 | -1.2776 | 0.28323 |  | Case 7 | Sec_V959595_F605660_dfdt4 | 10 | 0.95 | 0.95 | 0.95 | 0.95 | 56 | -4 | 60 | 1 | 0.1 | 0 | 0
| AngFrom5 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | [12 empty] | 260 | 0 | 0 | Freq2 | Case 8 | Sec_V959595_F605660_dfdt8 | 10 | 0.95 | 0.95 | 0.95 | 0.95 | 56 | -8 | 60 | 1 | 0.1 | 0 | 0
| AngTo5 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | [12 empty] | 265 | 1.2974 | -0.1708 | Vmag2pu | Case 9 | Sec_V909090_F605660_dfdt1 | 10 | 0.9 | 0.9 | 0.9 | 0.9 | 56 | -1 | 60 | 1 | 0.1 | 0 | 0
| FreqFrom5 | 60 | 60 | 60 | 60 | 56 | 56 | 60 | [12 empty] | 270 | 2.6047 | -0.22788 | dfdt2 | Case 10 | Sec_V909090_F605660_dfdt2 | 10 | 0.9 | 0.9 | 0.9 | 0.9 | 56 | -2 | 60 | 1 | 0.1 | 0 | 0
| FreqTo5 | 60 | 60 | 60 | 56 | 56 | 60 | 60 | [12 empty] | 275 | 3.9121 | -0.1708 | t2AddlTime | Case 11 | Sec_V909090_F605660_dfdt4 | 10 | 0.9 | 0.9 | 0.9 | 0.9 | 56 | -4 | 60 | 1 | 0.1 | 0 | 0
| TimeConst5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 280 | 5.2094 | 0 |  | Case 12 | Sec_V909090_F605660_dfdt8 | 10 | 0.9 | 0.9 | 0.9 | 0.9 | 56 | -8 | 60 | 1 | 0.1 | 0 | 0
| dq/dt | 0 | 29.6908 | 0 | -0.22268 | #DIV/0! | 0.11134 | #DIV/0! | [12 empty] | 285 | 6.487 | 0.28323 |  | Case 13 | Sec_V858585_F605660_dfdt1 | 10 | 0.85 | 0.85 | 0.85 | 0.85 | 56 | -1 | 60 | 1 | 0.1 | 0 | 0
| dPh/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [12 empty] | 290 | 7.735 | 0.67673 |  | Case 14 | Sec_V858585_F605660_dfdt2 | 10 | 0.85 | 0.85 | 0.85 | 0.85 | 56 | -2 | 60 | 1 | 0.1 | 0 | 0
| df/dt | 0 | 0 | 0 | -2 | #DIV/0! | 1 | #DIV/0! | [12 empty] | 295 | 8.944 | 1.1775 |  | Case 15 | Sec_V858585_F605660_dfdt4 | 10 | 0.85 | 0.85 | 0.85 | 0.85 | 56 | -4 | 60 | 1 | 0.1 | 0 | 0
| IC | State1 | State2 | State3 | State4 | State5 | State6 | State7 | [12 empty] | 300 | 10.1047 | 1.7817 |  | Case 16 | Sec_V858585_F605660_dfdt8 | 10 | 0.85 | 0.85 | 0.85 | 0.85 | 56 | -8 | 60 | 1 | 0.1 | 0 | 0
| MagFrom6 | 0 | 0 | 2.9691 | 2.9691 | 2.5237 | 2.5237 | 2.9691 | [12 empty] | 305 | 11.2084 | 2.4848 |  | Case 17 | Sec_V100100100_F606460_dfdt1 | 10 | 1 | 1 | 1 | 1 | 64 | 1 | 60 | -1 | 0.1 | 0 | 0
| MagTo6 | 0 | 2.9691 | 2.9691 | 2.5237 | 2.5237 | 2.9691 | 2.9691 | [12 empty] | 310 | 12.2465 | 3.2814 |  | Case 18 | Sec_V100100100_F606460_dfdt2 | 10 | 1 | 1 | 1 | 1 | 64 | 2 | 60 | -1 | 0.1 | 0 | 0
| AngFrom6 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | [12 empty] | 315 | 13.2113 | 4.1655 |  | Case 19 | Sec_V100100100_F606460_dfdt4 | 10 | 1 | 1 | 1 | 1 | 64 | 4 | 60 | -1 | 0.1 | 0 | 0
| AngTo6 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | [12 empty] | 320 | 14.0954 | 5.1303 |  | Case 20 | Sec_V100100100_F606460_dfdt8 | 10 | 1 | 1 | 1 | 1 | 64 | 8 | 60 | -1 | 0.1 | 0 | 0
| FreqFrom6 | 60 | 60 | 60 | 60 | 56 | 56 | 60 | [12 empty] | 325 | 14.892 | 6.1685 |  | Case 21 | Sec_V959595_F606460_dfdt1 | 10 | 0.95 | 0.95 | 0.95 | 0.95 | 64 | 1 | 60 | -1 | 0.1 | 0 | 0
| FreqTo6 | 60 | 60 | 60 | 56 | 56 | 60 | 60 | [12 empty] | 330 | 15.5951 | 7.2721 |  | Case 22 | Sec_V959595_F606460_dfdt2 | 10 | 0.95 | 0.95 | 0.95 | 0.95 | 64 | 2 | 60 | -1 | 0.1 | 0 | 0
| TimeConst6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 335 | 16.1993 | 8.4328 |  | Case 23 | Sec_V959595_F606460_dfdt4 | 10 | 0.95 | 0.95 | 0.95 | 0.95 | 64 | 4 | 60 | -1 | 0.1 | 0 | 0
| dq/dt | 0 | 29.6908 | 0 | -0.22268 | #DIV/0! | 0.11134 | #DIV/0! | [12 empty] | 340 | 16.7001 | 9.6418 |  | Case 24 | Sec_V959595_F606460_dfdt8 | 10 | 0.95 | 0.95 | 0.95 | 0.95 | 64 | 8 | 60 | -1 | 0.1 | 0 | 0
| dPh/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [12 empty] | 345 | 17.0936 | 10.8898 |  | Case 25 | Sec_V909090_F606460_dfdt1 | 10 | 0.9 | 0.9 | 0.9 | 0.9 | 64 | 1 | 60 | -1 | 0.1 | 0 | 0
| df/dt | 0 | 0 | 0 | -2 | #DIV/0! | 1 | #DIV/0! | [12 empty] | 350 | 17.3768 | 12.1674 |  | Case 26 | Sec_V909090_F606460_dfdt2 | 10 | 0.9 | 0.9 | 0.9 | 0.9 | 64 | 2 | 60 | -1 | 0.1 | 0 | 0
| VAref | State1 | State2 | State3 | State4 | State5 | State6 | State7 | [12 empty] | 355 | 17.5476 | 13.4648 |  | Case 27 | Sec_V909090_F606460_dfdt4 | 10 | 0.9 | 0.9 | 0.9 | 0.9 | 64 | 4 | 60 | -1 | 0.1 | 0 | 0
| MagFrom7 | 69.282 | 69.282 | 69.282 | 69.282 | 69.282 | 69.282 | 69.282 | [12 empty] | 360 | 17.6047 | 14.7721 |  | Case 28 | Sec_V909090_F606460_dfdt8 | 10 | 0.9 | 0.9 | 0.9 | 0.9 | 64 | 8 | 60 | -1 | 0.1 | 0 | 0
| MagTo7 | 69.282 | 69.282 | 69.282 | 69.282 | 69.282 | 69.282 | 69.282 | [16 empty] | Case 29 | Sec_V858585_F606460_dfdt1 | 10 | 0.85 | 0.85 | 0.85 | 0.85 | 64 | 1 | 60 | -1 | 0.1 | 0 | 0
| AngFrom7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | Case 30 | Sec_V858585_F606460_dfdt2 | 10 | 0.85 | 0.85 | 0.85 | 0.85 | 64 | 2 | 60 | -1 | 0.1 | 0 | 0
| AngTo7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | Case 31 | Sec_V858585_F606460_dfdt4 | 10 | 0.85 | 0.85 | 0.85 | 0.85 | 64 | 4 | 60 | -1 | 0.1 | 0 | 0
| FreqFrom7 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | [16 empty] | Case 32 | Sec_V858585_F606460_dfdt8 | 10 | 0.85 | 0.85 | 0.85 | 0.85 | 64 | 8 | 60 | -1 | 0.1 | 0 | 0
| FreqTo7 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | [16 empty] | Case 33 | Sec_V10085100_F605660_dfdt1 | 10 | 0.85 | 1 | 0.85 | 1 | 56 | -1 | 60 | 1 | 0.1 | 0 | 0
| TimeConst7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | Case 34 | Sec_V10085100_F605660_dfdt2 | 10 | 0.85 | 1 | 0.85 | 1 | 56 | -2 | 60 | 1 | 0.1 | 0 | 0
| dq/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [16 empty] | Case 35 | Sec_V10085100_F605660_dfdt4 | 10 | 0.85 | 1 | 0.85 | 1 | 56 | -4 | 60 | 1 | 0.1 | 0 | 0
| dPh/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [16 empty] | Case 36 | Sec_V10085100_F605660_dfdt8 | 10 | 0.85 | 1 | 0.85 | 1 | 56 | -8 | 60 | 1 | 0.1 | 0 | 0
| df/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [16 empty] | Case 37 | Sec_V10085100_F606460_dfdt1 | 10 | 0.85 | 1 | 0.85 | 1 | 64 | 1 | 60 | -1 | 0.1 | 0 | 0
| IAref | State1 | State2 | State3 | State4 | State5 | State6 | State7 | [16 empty] | Case 38 | Sec_V10085100_F606460_dfdt2 | 10 | 0.85 | 1 | 0.85 | 1 | 64 | 2 | 60 | -1 | 0.1 | 0 | 0
| MagFrom8 | 0 | 0 | 2.9691 | 2.9691 | 2.9691 | 2.9691 | 2.9691 | [16 empty] | Case 39 | Sec_V10085100_F606460_dfdt4 | 10 | 0.85 | 1 | 0.85 | 1 | 64 | 4 | 60 | -1 | 0.1 | 0 | 0
| MagTo8 | 0 | 2.9691 | 2.9691 | 2.9691 | 2.9691 | 2.9691 | 2.9691 | [16 empty] | Case 40 | Sec_V10085100_F606460_dfdt8 | 10 | 0.85 | 1 | 0.85 | 1 | 64 | 8 | 60 | -1 | 0.1 | 0 | 0
| AngFrom8 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | [16 empty] | Case 41 | Dep_V100100100_F605660_dfdt1 | -10 | 1 | 1 | 1 | 1 | 56 | -1 | 60 | 1 | 0.1 | 0 | 0
| AngTo8 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | [16 empty] | Case 42 | Dep_V100100100_F605660_dfdt2 | -10 | 1 | 1 | 1 | 1 | 56 | -2 | 60 | 1 | 0.1 | 0 | 0
| FreqFrom6 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | [16 empty] | Case 43 | Dep_V100100100_F605660_dfdt4 | -10 | 1 | 1 | 1 | 1 | 56 | -4 | 60 | 1 | 0.1 | 0 | 0
| FreqTo8 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | [16 empty] | Case 44 | Dep_V100100100_F605660_dfdt8 | -10 | 1 | 1 | 1 | 1 | 56 | -8 | 60 | 1 | 0.1 | 0 | 0
| TimeConst8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | Case 45 | Dep_V959595_F605660_dfdt1 | -10 | 0.95 | 0.95 | 0.95 | 0.95 | 56 | -1 | 60 | 1 | 0.1 | 0 | 0
| dq/dt | 0 | 29.6908 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [16 empty] | Case 46 | Dep_V959595_F605660_dfdt2 | -10 | 0.95 | 0.95 | 0.95 | 0.95 | 56 | -2 | 60 | 1 | 0.1 | 0 | 0
| dPh/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [16 empty] | Case 47 | Dep_V959595_F605660_dfdt4 | -10 | 0.95 | 0.95 | 0.95 | 0.95 | 56 | -4 | 60 | 1 | 0.1 | 0 | 0
| df/dt | 0 | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | [16 empty] | Case 48 | Dep_V959595_F605660_dfdt8 | -10 | 0.95 | 0.95 | 0.95 | 0.95 | 56 | -8 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 49 | Dep_V909090_F605660_dfdt1 | -10 | 0.9 | 0.9 | 0.9 | 0.9 | 56 | -1 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 50 | Dep_V909090_F605660_dfdt2 | -10 | 0.9 | 0.9 | 0.9 | 0.9 | 56 | -2 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 51 | Dep_V909090_F605660_dfdt4 | -10 | 0.9 | 0.9 | 0.9 | 0.9 | 56 | -4 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 52 | Dep_V909090_F605660_dfdt8 | -10 | 0.9 | 0.9 | 0.9 | 0.9 | 56 | -8 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 53 | Dep_V858585_F605660_dfdt1 | -10 | 0.85 | 0.85 | 0.85 | 0.85 | 56 | -1 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 54 | Dep_V858585_F605660_dfdt2 | -10 | 0.85 | 0.85 | 0.85 | 0.85 | 56 | -2 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 55 | Dep_V858585_F605660_dfdt4 | -10 | 0.85 | 0.85 | 0.85 | 0.85 | 56 | -4 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 56 | Dep_V858585_F605660_dfdt8 | -10 | 0.85 | 0.85 | 0.85 | 0.85 | 56 | -8 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 57 | Dep_V100100100_F606460_dfdt1 | -10 | 1 | 1 | 1 | 1 | 64 | 1 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 58 | Dep_V100100100_F606460_dfdt2 | -10 | 1 | 1 | 1 | 1 | 64 | 2 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 59 | Dep_V100100100_F606460_dfdt4 | -10 | 1 | 1 | 1 | 1 | 64 | 4 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 60 | Dep_V100100100_F606460_dfdt8 | -10 | 1 | 1 | 1 | 1 | 64 | 8 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 61 | Dep_V959595_F606460_dfdt1 | -10 | 0.95 | 0.95 | 0.95 | 0.95 | 64 | 1 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 62 | Dep_V959595_F606460_dfdt2 | -10 | 0.95 | 0.95 | 0.95 | 0.95 | 64 | 2 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 63 | Dep_V959595_F606460_dfdt4 | -10 | 0.95 | 0.95 | 0.95 | 0.95 | 64 | 4 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 64 | Dep_V959595_F606460_dfdt8 | -10 | 0.95 | 0.95 | 0.95 | 0.95 | 64 | 8 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 65 | Dep_V909090_F606460_dfdt1 | -10 | 0.9 | 0.9 | 0.9 | 0.9 | 64 | 1 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 66 | Dep_V909090_F606460_dfdt2 | -10 | 0.9 | 0.9 | 0.9 | 0.9 | 64 | 2 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 67 | Dep_V909090_F606460_dfdt4 | -10 | 0.9 | 0.9 | 0.9 | 0.9 | 64 | 4 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 68 | Dep_V909090_F606460_dfdt8 | -10 | 0.9 | 0.9 | 0.9 | 0.9 | 64 | 8 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 69 | Dep_V858585_F606460_dfdt1 | -10 | 0.85 | 0.85 | 0.85 | 0.85 | 64 | 1 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 70 | Dep_V858585_F606460_dfdt2 | -10 | 0.85 | 0.85 | 0.85 | 0.85 | 64 | 2 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 71 | Dep_V858585_F606460_dfdt4 | -10 | 0.85 | 0.85 | 0.85 | 0.85 | 64 | 4 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 72 | Dep_V858585_F606460_dfdt8 | -10 | 0.85 | 0.85 | 0.85 | 0.85 | 64 | 8 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 73 | Dep_V8510085_F605660_dfdt1 | -10 | 1 | 0.85 | 1 | 0.85 | 56 | -1 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 74 | Dep_V8510085_F605660_dfdt2 | -10 | 1 | 0.85 | 1 | 0.85 | 56 | -2 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 75 | Dep_V8510085_F605660_dfdt4 | -10 | 1 | 0.85 | 1 | 0.85 | 56 | -4 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 76 | Dep_V8510085_F605660_dfdt8 | -10 | 1 | 0.85 | 1 | 0.85 | 56 | -8 | 60 | 1 | 0.1 | 0 | 0
[25 empty] | Case 77 | Dep_V8510085_F606460_dfdt1 | -10 | 1 | 0.85 | 1 | 0.85 | 64 | 1 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 78 | Dep_V8510085_F606460_dfdt2 | -10 | 1 | 0.85 | 1 | 0.85 | 64 | 2 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 79 | Dep_V8510085_F606460_dfdt4 | -10 | 1 | 0.85 | 1 | 0.85 | 64 | 4 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | Case 80 | Dep_V8510085_F606460_dfdt8 | -10 | 1 | 0.85 | 1 | 0.85 | 64 | 8 | 60 | -1 | 0.1 | 0 | 0
[25 empty] | SecV100100_F6056_dfdt1 |  |  |  | 100 | 77 | 0.95 |  |  |  | 95
Sec_V10085100_f606460_dfdt2
[25 empty] | Dep_V10085100_f606460_dfdt8 | [6 empty] | -0.85 | 85
Note on B15: Note: The resistive reach setting is the per-phase fault resistance and not the loop fault resistance between phases. Many relays have are set using the loop fault resistance. If this is the case, devide the relay setting by 2 before entering it in this field.
Note on B17: For a point inside the characteristic (dependability test), enter a negative number.
Note on B21: This state stabilizes the relay with nominal voltage and frequency before the test. Current is zero.
Note on B22: To avold any waveform discontinuitiies and sudden jumps, the voltage and current are ramped to the starting point 0, to keep the relay stable.
Note on B31: Test current is calculated based on the specified voltage and load impedance.
Note on B37: Default value of duration for intitial condition when selecting one of the WG D22 cases.
Note on B38: When selecting a pre-defined test case using the dropdown box this will be the default impedance margin of the starting point 0 outside and inside the characteristic at the load angle.
Note on C19: Keeping the Impedance point constant during ramping of voltage will ramp also the current.
Note on F24: Frequency and voltage (and current if the "Keep Z test pt. constant" box is checked) will ramp from Point 0 to Point 1 at the specificed rates below.
Note on F31: Enter a negative number if requency is ramped down.
Note on F35: Frequency and voltage with remain constant during this period
Note on F38: Enter a duration of 0 to 0.2 s for the quadratic curve ramp; this increases the duration of the first ramp, Ramp1 duration.
Note on J31: Enter a negative number if requency is ramped down.
Note on J35: Frequency and voltage with remain constant during this period.

## RampStates (hidden)
This is a Generic Worksheet that can be used for by other worksheets
COMTRADE Information | [5 empty] | File Name (use if entered here) | Sec_V10085100_F605660_dfdt4
ComtradeStationName | IEEE PSRC WG D22
ComtradeCircuitName | Line 1 |  |  |  |  | Header Info (use if entered here) | Sec_V10085100_F605660_dfdt4 file tests relay security for varying frequency. Inital voltage at 1 pu and nominal frequency. Freq. ramps to 56Hz at -4Hz/s, then back to init. freq. at 1Hz/s. Voltage ramps to 0.85 pu, then back to 1 pu.
ComtradeSystemFrequency | 60 | Hz
ComtradeSamplingRate | 10000 | /s |  |  |  | StateTransitionAngleHandling | 0 | Use preceding sample or Jump to new state phase angle or Adjust to current angle difference
NoOfSources | 8
Sources | SourceNumber | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | [6 empty] | NoOfDigitals=0
| SourceNames | VA | VB | VC | IA | IB | IC | VAref | IAref | V2C | I2A | I2B | I2C | [6 empty] | ComtradeFormat = "ASCII"
| SourceUnit | [18 empty] | ComtradeYear=1999 | bar: 1 to 12
NoOfStatesRamps | 7 | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
Duration | 7: tStateRamp; State1: 0.1; State2: 0.1; State3: 0.1; State4: 1; State5: 0; State6: 4; State7: 0
Source 1 | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
VA | MagFrom1 | 0.1 State1: 69.282; 0.1 State2: 69.282; 0.1 State3: 69.282; 1 State4: 69.282; 0 State5: 58.8897; 4 State6: 58.8897; 0 State7: 69.282
| MagTo1 | 0.1 State1: 69.282; 0.1 State2: 69.282; 0.1 State3: 69.282; 1 State4: 58.8897; 0 State5: 58.8897; 4 State6: 69.282; 0 State7: 69.282
| AngFrom1 | 0.1 State1: 0; 0.1 State2: 0; 0.1 State3: 0; 1 State4: 0; 0 State5: 0; 4 State6: 0; 0 State7: 0
| AngTo1 | 0.1 State1: 0; 0.1 State2: 0; 0.1 State3: 0; 1 State4: 0; 0 State5: 0; 4 State6: 0; 0 State7: 0
| FreqFrom1 | 0.1 State1: 60; 0.1 State2: 60; 0.1 State3: 60; 1 State4: 60; 0 State5: 56; 4 State6: 56; 0 State7: 60
| FreqTo1 | 0.1 State1: 60; 0.1 State2: 60; 0.1 State3: 60; 1 State4: 56; 0 State5: 56; 4 State6: 60; 0 State7: 60
| TimeConst1 | 0.1 State1: 0; 0.1 State2: 0; 0.1 State3: 0; 1 State4: 0; 0 State5: 0; 4 State6: 0; 0 State7: 0
| dq/dt | 0.1 State1: 0; 0.1 State2: -2.7713; 0.1 State3: #DIV/0!; 1 State4: 1.7321; 0 State5: #DIV/0!
| dPh/dt | 0.1 State1: 0; 0.1 State2: 0; 0.1 State3: #DIV/0!; 1 State4: 0; 0 State5: #DIV/0!
| df/dt | 0.1 State1: 0; 0.1 State2: -2; 0.1 State3: #DIV/0!; 1 State4: -1; 0 State5: #DIV/0!
Source Name | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
VB | MagFrom2 | 0 State1: 69.282; -2 State2: 69.282; #DIV/0! State3: 69.282; -1 State4: 69.282; #DIV/0! State5: 58.8897; #DIV/0! State6: 58.8897; #DIV/0! State7: 69.282
| MagTo2 | 0 State1: 69.282; -2 State2: 69.282; #DIV/0! State3: 69.282; -1 State4: 58.8897; #DIV/0! State5: 58.8897; #DIV/0! State6: 69.282; #DIV/0! State7: 69.282
| AngFrom2 | 0 State1: 240; -2 State2: 240; #DIV/0! State3: 240; -1 State4: 240; #DIV/0! State5: 240; #DIV/0! State6: 240; #DIV/0! State7: 240
| AngTo2 | 0 State1: 240; -2 State2: 240; #DIV/0! State3: 240; -1 State4: 240; #DIV/0! State5: 240; #DIV/0! State6: 240; #DIV/0! State7: 240
| FreqFrom2 | 0 State1: 60; -2 State2: 60; #DIV/0! State3: 60; -1 State4: 60; #DIV/0! State5: 56; #DIV/0! State6: 56; #DIV/0! State7: 60
| FreqTo2 | 0 State1: 60; -2 State2: 60; #DIV/0! State3: 60; -1 State4: 56; #DIV/0! State5: 56; #DIV/0! State6: 60; #DIV/0! State7: 60
| TimeConst2 | 0 State1: 0; -2 State2: 0; #DIV/0! State3: 0; -1 State4: 0; #DIV/0! State5: 0; #DIV/0! State6: 0; #DIV/0! State7: 0
dq/dt
dPh/dt
df/dt
Source Name | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
VC | MagFrom3 | State1: 69.282; State2: 69.282; State3: 69.282; State4: 69.282; State5: 58.8897; State6: 58.8897; State7: 69.282
| MagTo1 | State1: 69.282; State2: 69.282; State3: 69.282; State4: 58.8897; State5: 58.8897; State6: 69.282; State7: 69.282
| AngFrom3 | State1: 120; State2: 120; State3: 120; State4: 120; State5: 120; State6: 120; State7: 120
| AngTo3 | State1: 120; State2: 120; State3: 120; State4: 120; State5: 120; State6: 120; State7: 120
| FreqFrom3 | State1: 60; State2: 60; State3: 60; State4: 60; State5: 56; State6: 56; State7: 60
| FreqTo3 | State1: 60; State2: 60; State3: 60; State4: 56; State5: 56; State6: 60; State7: 60
| TimeConst3 | State1: 0; State2: 0; State3: 0; State4: 0; State5: 0; State6: 0; State7: 0
dq/dt
dPh/dt
df/dt
Source Name | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
IA | MagFrom4 | State1: 0; State2: 0; State3: 2.5237; State4: 2.5237; State5: 2.5237; State6: 2.5237; State7: 2.5237
| MagTo4 | State1: 0; State2: 2.5237; State3: 2.5237; State4: 2.5237; State5: 2.5237; State6: 2.5237; State7: 2.5237
| AngFrom4 | State1: 325; State2: 325; State3: -35; State4: -35; State5: -35; State6: -35; State7: -35
| AngTo4 | State1: 325; State2: 325; State3: -35; State4: -35; State5: -35; State6: -35; State7: -35
| FreqFrom4 | State1: 60; State2: 60; State3: 60; State4: 60; State5: 56; State6: 56; State7: 60
| FreqTo4 | State1: 60; State2: 60; State3: 60; State4: 56; State5: 56; State6: 60; State7: 60
| TimeConst4 | State1: 0; State2: 0; State3: 0; State4: 0; State5: 0; State6: 0; State7: 0
dq/dt
dPh/dt
df/dt
Source Name | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
IB | MagFrom5 | State1: 0; State2: 0; State3: 2.5237; State4: 2.5237; State5: 2.5237; State6: 2.5237; State7: 2.5237
| MagTo5 | State1: 0; State2: 2.5237; State3: 2.5237; State4: 2.5237; State5: 2.5237; State6: 2.5237; State7: 2.5237
| AngFrom5 | State1: 205; State2: 205; State3: 205; State4: 205; State5: 205; State6: 205; State7: 205
| AngTo5 | State1: 205; State2: 205; State3: 205; State4: 205; State5: 205; State6: 205; State7: 205
| FreqFrom5 | State1: 60; State2: 60; State3: 60; State4: 60; State5: 56; State6: 56; State7: 60
| FreqTo5 | State1: 60; State2: 60; State3: 60; State4: 56; State5: 56; State6: 60; State7: 60
| TimeConst5 | State1: 0; State2: 0; State3: 0; State4: 0; State5: 0; State6: 0; State7: 0
dq/dt
dPh/dt
df/dt
Source Name | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
IC | MagFrom6 | State1: 0; State2: 0; State3: 2.5237; State4: 2.5237; State5: 2.5237; State6: 2.5237; State7: 2.5237
| MagTo6 | State1: 0; State2: 2.5237; State3: 2.5237; State4: 2.5237; State5: 2.5237; State6: 2.5237; State7: 2.5237
| AngFrom6 | State1: 85; State2: 85; State3: 85; State4: 85; State5: 85; State6: 85; State7: 85
| AngTo6 | State1: 85; State2: 85; State3: 85; State4: 85; State5: 85; State6: 85; State7: 85
| FreqFrom6 | State1: 60; State2: 60; State3: 60; State4: 60; State5: 56; State6: 56; State7: 60
| FreqTo6 | State1: 60; State2: 60; State3: 60; State4: 56; State5: 56; State6: 60; State7: 60
| TimeConst6 | State1: 0; State2: 0; State3: 0; State4: 0; State5: 0; State6: 0; State7: 0
dq/dt
dPh/dt
df/dt
Source Name | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
VAref | MagFrom7 | State1: 69.282; State2: 69.282; State3: 69.282; State4: 69.282; State5: 69.282; State6: 69.282; State7: 69.282
| MagTo7 | State1: 69.282; State2: 69.282; State3: 69.282; State4: 69.282; State5: 69.282; State6: 69.282; State7: 69.282
| AngFrom7 | State1: 0; State2: 0; State3: 0; State4: 0; State5: 0; State6: 0; State7: 0
| AngTo7 | State1: 0; State2: 0; State3: 0; State4: 0; State5: 0; State6: 0; State7: 0
| FreqFrom7 | State1: 60; State2: 60; State3: 60; State4: 60; State5: 60; State6: 60; State7: 60
| FreqTo7 | State1: 60; State2: 60; State3: 60; State4: 60; State5: 60; State6: 60; State7: 60
| TimeConst7 | State1: 0; State2: 0; State3: 0; State4: 0; State5: 0; State6: 0; State7: 0
dq/dt
dPh/dt
df/dt
Source Name | IAref | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
IAref | MagFrom8 | State1: 0; State2: 0; State3: 2.5237; State4: 2.5237; State5: 2.5237; State6: 2.5237; State7: 2.5237
| MagTo8 | State1: 0; State2: 2.5237; State3: 2.5237; State4: 2.5237; State5: 2.5237; State6: 2.5237; State7: 2.5237
| AngFrom8 | State1: 325; State2: 325; State3: 325; State4: 325; State5: 325; State6: 325; State7: 325
| AngTo8 | State1: 325; State2: 325; State3: 325; State4: 325; State5: 325; State6: 325; State7: 325
| FreqFrom8 | State1: 60; State2: 60; State3: 60; State4: 60; State5: 60; State6: 60; State7: 60
| FreqTo8 | State1: 60; State2: 60; State3: 60; State4: 60; State5: 60; State6: 60; State7: 60
| TimeConst8 | State1: 0; State2: 0; State3: 0; State4: 0; State5: 0; State6: 0; State7: 0
dq/dt
dPh/dt
df/dt
Source Name | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
V2C | MagFrom1 | State1: 100; State2: 90
| MagTo1 | State1: 90; State2: 110
AngFrom1
AngTo1
FreqFrom1
FreqTo1
TimeConst1
dq/dt
dPh/dt
df/dt
Source Name | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
I2A | MagFrom1 | State1: 100; State2: 90
| MagTo1 | State1: 90; State2: 110
AngFrom1
AngTo1
FreqFrom1
FreqTo1
tStateRamp1
TimeConst1
dq/dt
dPh/dt
df/dt
Source Name | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
I2B | MagFrom1 | State1: 100; State2: 90
| MagTo1 | State1: 90; State2: 110
AngFrom1
AngTo1
FreqFrom1
FreqTo1
TimeConst1
dq/dt
dPh/dt
df/dt
Source Name | Table Names | State1 | State2 | State3 | State4 | State5 | State6 | State7 | State8 | State9 | State10 | State11 | State12 | State13 | State14 | State15 | State16 | State17 | State18 | State19 | State20
I2C | MagFrom1 | State1: 100; State2: 90
| MagTo1 | State1: 90; State2: 110
AngFrom1
AngTo1
FreqFrom1
FreqTo1
TimeConst1
dq/dt
dPh/dt
df/dt
Note on H6: 0=Use phase angle of preceding SAMPLE, 1=Jump to new STATE FromAngle, 2=Use current SAMPLE angle and adjust to difference between angles of consecutive STATES (ToAngle of preceding state and FromAngle of new state) =current angle + (newFromAngle - preToAngle)