## Slide 1: Emtp Tutorial
Sponsored
By
The Power System Relaying
Committee
IEEE PES

## Slide 2: Authors
Mr. Demetrios Tziouvaras
Mr. Jules Esztergalyos
Mr. Charlie Henville
Dr. Ljubomir Kojovic
Dr. Peter McLaren
Dr. Moh Sachdev
Dr. Tarlochan Sidhu
Dr. Mietek Glinkowski

## Slide 3: Tutorial Presenters
Mr. Demetrios Tziouvaras
Mr. Charlie Henville
Dr. Ljubomir Kojovic
Dr. Peter McLaren
Dr. Moh Sachdev
Dr. Tarlochan Sidhu

## Slide 4: Agenda
08:00 – 08:15 Welcome & Introductions
08:15 – 09:15 Tarlochan Sidhu
09:15 – 10:00 Charlie Henville
10:00 – 10:15 Break
10:15 – 11:00 Peter McLaren
11:00 – 12:00 Demetrios Tziouvaras
12:00 – 01:00 Lunch

## Slide 5: Agenda
01:00 – 01:45 Demetrios Tziouvaras
01:45 – 02:30 Ljubomir Kojovic
02:30 – 03:15 Ljubomir Kojovic
03:15 – 03:30 Break
03:30 – 04:15 Demetrios Tziouvaras
04:15 – 05:00 Monhidar Sachdev
05:00 – 05:30 Q&A and Adjourn

## Slide 6: Contents
Introduction
  Why we need emtp?
  Modern transient programs
Basics
  Transient solution
  Component and circuit representation
  Practical issues
Notes: 1

## Slide 7: Why Emtp?
Conventional Studies
  Steady-state analysis
    Load flow and fault analysis
Rs
Xs
Rf
Xf
Es
Vf
If
Notes: 2

## Slide 8: Why Emtp?
Dynamic analysis
    Stability studies
Steam
Gov.
w
AVR
Vt
L
O
A
D
Notes: 2

## Slide 9: Why Emtp?
Transient Analysis
  Harmonics and non-linearities
    emtp
Notes: 2

## Slide 10: Modern Emtps
Several Commercial Programs
  EMTDC, EMTP, ATP, MORGAT …….
Features
  User-friendly
  Graphics and auxiliary programs
  Model libraries and custom models
  Interface to other software
  Less training time
Notes: 2

## Slide 11: Transient Solution
1
)
1
(
*
1
v
dt
i
d
L
e
+
=
2
2
*
2
1
v
R
i
v
+
=
dt
v
d
C
i
)
2
(
*
2
2
=
1
1
2
1
R
v
i
i
+
=
Notes: 2

## Slide 12: Inductance Model
Notes: 2

## Slide 13: Numerical Integration
t
time
v
v
k,m
(t)
v
k,m
(t-
D
T
)
(t-
D
T)
Average
value
unknown
v
k,m
Notes: 2

## Slide 14: Inductance Model
Notes: 2

## Slide 15: Capacitance Model
Notes: 2

## Slide 16: Resistance Model
i
k,m
(t)
v
km
(t)
k
m
R
Notes: 2

## Slide 17: Circuit Representation
Notes: 2

## Slide 18: Circuit Representation
ú
ú
ú
û
ù
ê
ê
ê
ë
é
D
+
-
-
+
+
D
)
2
/
(
1
1
1
1
1
1
)
/
2
(
1
2
12
12
12
12
1
1
C
T
R
R
R
R
R
T
L
v
t
v
t
1
2
(
)
(
)
é
ë
ê
ù
û
ú
=
ú
ú
û
ù
ê
ê
ë
é
D
+
2
1
1
)
/
2
(
)
(
C
L
I
T
L
t
e
I
Notes: 2

## Slide 19: Switching
Consider R12 as a switch
Notes: 2

## Slide 20: Switching
Conductance matrix value will change
ú
ú
ú
û
ù
ê
ê
ê
ë
é
D
+
-
-
+
+
D
)
2
/
(
1
1
1
1
1
1
)
/
2
(
1
2
12
12
12
12
1
1
C
T
R
R
R
R
R
T
L
v
t
v
t
1
2
(
)
(
)
é
ë
ê
ù
û
ú
=
ú
ú
û
ù
ê
ê
ë
é
D
+
2
1
1
)
/
2
(
)
(
C
L
I
T
L
t
e
I
Notes: 2

## Slide 21: Switching
Effect of switch resistance
Notes: 2

## Slide 22: Time Step
Period of natural frequency is about 1.5 ms
Notes: 2

## Slide 23: Time Step
Time step of 1.0 ms
Notes: 2

## Slide 24: Time Step
Time step of 5 micro-seconds
Notes: 2

## Slide 25: Time Step
Time step of 70 micro-seconds
Notes: 2

## Slide 26: Other Components
Non-linear and time-varying components
Transmission lines
Mutual Coupling
Multiphase networks
Notes: 2

## Slide 27: Practical Issues
Accuracy and stability of calculations
  Trapezoidal rule
  Extrapolation
Triangular factorization and sparsity
  Reduces computer time and memory
Subsystems
  Takes advantage of time delay
  Reduces time and simplifies calculations
Notes: 2

## Slide 28: Subsystems
Nodal conductance matrix
Notes: 2

## Slide 29: Concluding Remarks
Many protection applications can be studied using conventional programs.
Emtp studies are becoming important as relay operating times reduce and systems become more non-linear.
Emtp should not be used as a black box but confidence should be developed by understanding program’s operation and that of the system under study.
MORE DETAILS ……….
Notes: 2

## Slide 30: emtp Applications and Fault Induced Transients
Notes: Transient studies are widely used in power systems world wide to study phenomena which are not fundamental frequency. This section will focus on applications which are relevant to protection engineers.
emtp started off with being the study of relatively high frequency phenomena such as switching surges, but has since been extended to include lower frequency, longer durations. Now used for a wide variety of studies, including those of interest to us.
This slide shows one type of high frequency phenomenon which is sometimes of interest, that is the inrush to a shunt capacitor. We sometimes need to know how to set a relay to be sure it overrides this current and doesn’t operate unexpectedly. emtp will generate simulated waveforms which can be used to check the relay response, as we’ll see later

## Slide 31: emtp Studies
Steady State Solution - Precondition for Transient studies, but useful in itself.
Transient Solution - step by step integration, knowing the previous solution (starting from steady state).
Notes: We’ll look at both sides of transient studies, the steady state solution, which is a precondition for the transient solution, (because we have to check the transient response from some known starting point) and the transient solution itself. These two phases of the study are semi independent. You can run the first without the second, but not vice versa.
first the ss solution

## Slide 32: Steady State Solution
Fully represented system - phasor solution.
Unbalanced primary system
  Non transposed lines
  Unequal length lines (cables)
  Different transformers/phase
  Series capacitor 1 phase bypass
Cross country faults
Effect of underbuild, - railway lines
Notes: Because it is a steady state solution, all the output is in phasor quantities. All the exciting voltage or current sources have to be at fundamental frequency.
An interesting observation however, that the solution is on a phase by phase basis, representing all phases and other conductors individually. Thus not only can the primary system be unbalanced, but the effects of nearby conductors, not necessarily part of the power system can be checked.
Non transposed lines is one obvious application. I once had some difficulty in using the assumption of balanced phases for fault location on a long 138 kV line, and used the emtp to see if the fault location estimation could provide different answers for faults in different phases at the same locations (it didn’t for that exercise).
500 kV submarine cables produce system unbalances worse at light loads.
KLY tfr replacement example. ss load and fault performance.
series caps bypass, or single phase open for extended periods, check effect on system unbalance.
cross country faults, everything in physical units - faults between different voltage levels. 230 kV to 60 kV at 1.0 p.u. produces no current!
railway lines, gas pipelines, distribution underbuild. All can be modelled in ss.
Note that fundamental frequency faults can be studied in ss too if desired for a special reason.

## Slide 33: System Harmonics
Harmonic distortion of 138 kV supply
Notes: ss solution doesn’t have to be at the fundamental frequency either. It can be at any frequency or set of frequencies desired. As long as all you want for the output is a phasor solution at the frequency of interest. A note of caution however, when deviating significantly from the power system frequency, you have to be careful that you know the system parameters. e.g. skin effect can change resistance. Zero sequence impedance of transmission line (in henries) is highly frequency dependent. However, a sweep of frequency response at a range of frequencies can be helpful for identifying system resonances.
see this slide of a location in the north of BC where a long (>200 mile) 138 kV line exhibited a very distorted supply voltage. It caused problems in the system, especially during GICs when there was a lot of harmonic excitation. In fact, high peak voltages caused a surge arrester failure, and some customer’s equipment was damaged by overvoltages.
frequency scan in emtp discovered the resonance and was used to investigate various mitigation methods. No means of detuning the resonance was found to be practical. All that was done was to put a capacitor in the neutral of the transformer at the north end of the line so that GIC couldn’t flow in the transformer to excite the resonance. Other things still excite it; so we still have bad distortion of this supply, but the degree has been reduced.

## Slide 34: System Harmonics
Impedance scan
Notes: This shows the output of a series of emtp solutions at a variety of frequencies. all that is done is to put a 1 kv sine wave voltage and measure the current flows and voltages at various frequencies and locations and calculate the apparent impedance. the resonance points jump right out. first point is at 240 Hz in this case.
With plots like this, its easy to se the effects of the various mitigation methods.
So ss solutions at fundamental are helpful for ss system unbalances, quasi ss conditions (SC) and for resonance investigations at various frequencies.

## Slide 35: emtp Studies
Steady State Solution - Precondition for Transient studies, but useful in itself.
Transient Solution - step by step integration, knowing the previous solution (starting from steady state).
Notes: Having finished with the ss solution, we’ll consider the true transient study now. Well look first at a very simple glimpse into the workings of the program so that it becomes de-mystified a bit, then consider the various applications in protection studies.

## Slide 36: Time Step Size (I)
(About 5 - 10 time steps per period of the highest frequency of interest)
Notes: we can imagine that choosing the right time step is a very important part of a transient study. Generally speaking the shorter the time step, the more accurate the solution. However, it is also more computationally expensive. No need to do smaller time steps than encessary. This table lists some types of phenomena that might be of interest, and the sixe of step and approximate duration of study. These are of course just “order of magnitude” numbers.
Discuss computation time for emtp studies. 4 nodes 1 source, 1 inductor, 1 capacitor and 1 resistor. Home made spread sheet did it in 15 minutes. microtran did it in 2 seconds. aim is for real time.

## Slide 37: Time Step Size (II)
FACTS
M
D t3 =50m s
D t4 =10m s
D t5 =20ms
Dt1 =1s
Dt2 =1ms
(Diagram courtesy of Dr. J. Marti, University of BC)
Approx. order of magnitude of time step, considering some
frequencies of interest for equipment being studied.
(Conventional studies use a single time step for the whole system)
Notes: As well as considering the phenomena of interest, we might also consider the equipment being studied and the maximum frequency that might be of interest in any particular one. In the case of a turbine, and its controls, periods of phenomena might be in the range of several seconds or tens of seconds; so we see quite a long time step. Frequencies of switching surges in transmission lines are in the range of some kilohertz, depending on line length. Solid state controllers might need higher frequency investigation, and motors maybe longer. Conventional studies however, use just one frequency. Therefore, we have to choose the highest frequency of interest. UBC is presently developing a real time emtp which might run different parts of the system at different time steps.

## Slide 38: Transients
AC network faults
Single phase switching
High speed reclosing
Energizations/denergizations
Instrument transformers
rotating machines
Non-linear elements
Notes: We’re finished now with the theory of emtp, well look at some of the applications. Here is a list of some of them.
Faults - check true transients and effects on relays
SPT check protection
high speed reclosing - check effect of trapped charge on voltage elements
energizations - denergizations are notorious
instrument transformers, particularly cts, but cvts too.
rotating machines dynamic studies could be sufficient, but transient studies OK too. especially if shaft oscillations are involved (e.g. SSR)
non linear elements introduce all sorts of strange effects including harmonics that need investigating.

## Slide 39: Fault induced transients
Transient dc component
Higher frequency transients
Near fundamental frequency transients

## Slide 40: Transient DC Component
Notes: The most common type of transient in short circuits is the transient dc offset of short circuit currents which occur because the current in an inductive circuit cannot change instantaneously to the fault level.

## Slide 41: Higher Frequency Transients 1

## Slide 42: Higher Frequency Transients 2

## Slide 43: (Not so) High Frequency Transients 3
285 km. 500 kV line (no CVT model)

## Slide 44: Series Capacitor Resonance

## Slide 45: Network Faults
(500 kV Circuit, with series capacitor)
Notes: reverse fault. hard to determine the fundamental frequency component.
can see low frequency and high frequency and no frequency at all
can use this type of signal to test relays

## Slide 46: Relay Filters
May need to be sharply tuned
Sharper tuning, longer delay
Special filter designs
Caution with high sampling frequency digital relays.

## Slide 47: Transformer Inrush
(90 MVA Transformer, energized from 230 kV cable circuit)
Notes: Tfr inrush is a classic. Can check for magnitude of currents, and for harmonics.
Check inst. o/c relays don’t operate for inrush, check there are enough harmonics to restrain diff relays.
can use spreadsheet to check harmonics or analyse directly with so called post processing programs
deviate to talk about post and pre processing.
Check the effect on harmonics of connected lines and capacitor banks.

## Slide 48: Differentially connected cts
(Custom built transient program)
Notes: Here’s an example of a custom built transients program which is not emtp. Came about because in the early days we found the emtp too cumbersome. Like using a sledgehammer to crack a nut.
home made program is limited to 60 Hz excitation only, but can simulate ct performance quite well. We use it to check the effect of high burden. high offset, high primary time constant systems.
Ever wonder what sort of slope would be required on a percentage restrained differential relay to override this type of signal? Well just inject it into the relay.

## Slide 49: Cranbrook 500 kV Substation
DFR
DFR
5MB1
5L92
5L94
To 230 kV
To 230 kV
87
BS
87
B
Lightning
Arrestor
Transformer
T1
Notes: not all transients yield to emtp tests (at least not easily)
real life transients problem at Cranbrook substation.
explain Surge arresters, and DFR locations
explain two different types of high impedance relays, one misoperated and one didn’t.

## Slide 50: A Real World Signal (During Lightning Storm)
Notes: explain bus protection misop.
difficulty of modeling when the relay non linear burden itself is a factor
difficulty of spending a lot of money to investigate.
explain “near miss” of line protection. Good history, no need for further investigation.

## Slide 51: Playback Test System
emtp simulation
(Or recorded data)
test input file
D/A converter(s)
amplifier(s)
relay(s) under test
monitoring eq'pt.
Low Level
Test Alternative
If relay(s) under test
affect power system
being simulated,
response to simulated
signals must be estimated
or determined by trial
and error.
Notes: We can use digitally recorded data to check relay response. The data could either be recorded from an actual disturbance, or from an emtp simulation.
However it is generated, it can be put into a test input file.
COMTRADE standard defines a standard format for the file. mention COMTRADE.
The file is then converted to analogue signals, and amplified to the correct level before being injected into the relay. Monitoring equipment will record relay inputs and outputs.
The amplifier is rather a difficult animal to design because it has to have a good frequency response and capability to drive high frequency through inductive burden (high voltage). DC coupled is best to get dc outputs as well.
many modern relays have low level inputs to allow use with low energy transducers. Can use these inputs to connect to low level outputs to avoid the need for expensive and heavy amplifiers. This is fine as long as you are sure the input transformers on the relay do not affect the measured signal.
Low level or high level, since we are using a prerecorded file, if the relay affects the system (e.g. opens a breaker) we have to guestimate when it is going to do this in order to open the breaker at the right time in the simulation. This may take some trial and error to get the simulation right.
Must also be careful to get enough pre-fault simulation to simulate real life conditions, e.g., polarizing memory in the relay must be full charged, (if applicable)

## Slide 52: Real Time Model Power System
emtp simulation
D/A converter(s)
amplifier(s)
relay(s) under test
monitoring eq'pt.
No need to “guesstimate”
relay response.
Real time
feedback
Notes: This slide has two major differences from the last. A feedback loop from the relay to the simulation computer, and no data file.
The feedback loop allows the relay to alter the state of the modeled system in real time to change the simulation parameters “on the fly”. Since everything happens in real time, there is no need for a data file, the data just streams on and on.
This takes all the guess work out of the simulation and ensures full “real life” conditions.
Issues about the power amplifiers and low level relay inputs are the same as in the previous slide.

## Slide 53: Cautions on Transient Tests
Not to be confused with Dynamic Tests
Data Decimation (beware of aliasing)
Influence of relay burden on measured signals
Notes: It might be possible to confuse transient tests with dynamic state tests. The dynamic tests are like switching a current source on suddenly to check relay response. The required signals to be measured are pre calculated, usually by a fault study, then switched to the correct magnitude and phase angle suddenly. There is no reproduction of any of the transients one encounters in real life. This type of testing is often quite satisfactory, because, as we know the relays filter out all the transients anyway, but it is not the same as transient testing.
The other thing about emtp simulations is that they use quite short time steps. In the order of 50 microseconds. This means that the sampling frequency is of the order of 20 kHz. So for a one second simulation there are 20,000 data points. When we consider there might be 12 channels of data, we can appreciate there could be a lot of data. this makes handling the files rather bulky. given normal relaying sampling rates of 960 Hz, there is a natural inclination to reduce the sampling frequency of the data files by simply storing every nth point. This is not a good idea, because if high frequency components are present, they can be amplified by aliasing. Therefore it is usually a good idea to apply a low pass filter first before removing the data points. The low pass filter can be a digital filter. The COMTRAD standard gives an example of a program that can do this.
Finally, we have to be aware that many electromechanical relays actually affect the performance of the transducers they are connected to. The high impedance diff relays are one example, but an induction disc relay is another. The amplifiers put out whatever signal the simulation tells them to. If the relay burden is significant. the simulation should include it too.

## Slide 54: Relay Models
Can be built into emtp
Can be “hooked on to” emtp
Can be run with emtp files
  Need no wires or hardware
  Allow you to “see inside” relay
  Not the same as actual relay
Notes: Relay models are another useful tool related to emtp studies. These are software models of the relay which can be subjected to the same transient tests as the actual relay. In the case of models, we don’t need any amplifiers, or D/A converters. We don’t even need any wires to connect anything, or monitoring equiment since the model will normally collect its own data.
The models can be a part of the emtp simulation, being built right into it, or can be another piece of software which is simply fed the data from the simulation. In the case of the separate software, it can be completely separate and function like a playback system, or can be hooked onto emtp so that it can feed back and affect the simulation. In this second case, the simulation doesn’t need to be in real time.
The models have several benefits. Listed above.

## Slide 55: Conclusions
emtp useful for
  Steady state (system unbalances or harmonics)
  Transient studies
Transient studies useful for
  Analysis of signals used by relays
  Test of relay response to transients
Cautions
  Fully understand the simulation process
  Select appropriate time step size
  Model only the detail needed
  Be careful during data decimation
Notes: These are the conclusions.
Be interested to know how many attendees here are aware that anyone in their company has used a transient program for some protection purpose.
How many have used emtp themselves for simulations with respect to protection performance?

## Slide 56: Thevenin source representation
V
oc
Network
Network
I
sc
Z
Thevenin
Z
Thevenin
=
V
oc
I
sc
V
oc

## Slide 57: Symmetrical Components - Thevenin
Zp
+
Zp
Zo
-
0
Thevenin equivalents
for the sequence networks
as seen from the location
where the equivalent source
is to be connected.
V
oc

## Slide 58: Calculation of Z’s
Zp
Zp
Zo
V
oc
+
-
0
I
f
If Voc is taken as 1, then
= 1/(2Zp + Zo)
Zp
V
oc
+
I
f
= 1/Zp
I
f

## Slide 59: Phase domain versus sequence Z’s
,

## Slide 60: Negative mutuals?
Looking in at this busbar
Because of the delta winding, which inserts a short circuit at the transformer
location in the zero sequence network, the zero sequence impedance is less than
the positive sequence impedance as seen from the system to the right.

## Slide 61: Conditions
The impedances calculated at 60Hz and the R and L values derived from them are only accurate at 60Hz.
In a switching study, where the shape of a wavefront is important, then the parameters used for the source should be measured at a much higher frequency.
For transmission lines the surge impedance should be used.

## Slide 62
1
2
3
4
Line 1 is represented in detail but lines 2,3 and 4 form the source at the busbar termination
of line 1. It is also assumed that there is no coupling between lines 1 and 2 for this simple
example. If the surge impedance of each line is 450 ohms then we have
150
1

## Slide 63
The previous slide showed a simple single phase transmission line such as you might
find in a signals application. In a 3-phase power line application, assuming a
symmetrical line configuration, we would have an aerial mode surge
impedance of , and a ground mode surge impedance of
1
For a study of this type it is much more likely that we would use a frequency
dependent model for the transmission lines.

## Slide 64
All major components of power systems have frequency dependent
impedances. Depending on the spectrum of interest it may be
possible to assume a constant value for a particular study. When a
source contains elements with frequency dependent parameters in
the bandwidth of interest then an attempt must be made to model
this dependence. The results of not doing so are shown on the next
slide.
A compromise solution might be to place a resistor of value
Zps in parallel with the 60Hz impedance. This is also shown on
the next slide.

## Slide 65: Effects of various source types

## Slide 66: Conclusions
Make sure the source representation involves the dominant effects which apply in the study under investigation.
This may be frequency dependence or a significant non-linearity in terms of a machine, transformer or an MOV protected series capacitor.

## Slide 67: Machine Models
The simplest model is that of a constant speed ( frequency) machine consisting of an ideal voltage source behind an appropriate impedance. For an electromagnetic transient study this would most likely be the machine subtransient reactance.
E``
X``

## Slide 68
This type of machine model would be appropriate in a study
where the transmission line being protected was represented
by lumped impedances and the time scale of interest was several
cycles. The relay bandwidth would be restricted to 60Hz and dc
offset components. e.g.
jX
E``
jX``
R
Machine
jx
Trans.
Line
Infinite BB
R
Relay

## Slide 69: For longer time periods involving possible power swings then the transient reactance would replace the subtransient reactance and the machine inertia would have to be represented by at least a single equivalent mass. The moment of inertia, J, is for both the turbine generator and exciter combined.
X`
E`
Inertia, J
Tm
Te

## Slide 70: Equation of motion
If the shaft angle is measured with respect to a stationary reference
where is an axis rotating at synchronous
speed and is the angle between a reference point on the rotor and this synchronously rotating axis. The shaft angular velocity is
. The equation of motion under swing
conditions is , where the slip, ,gives rise to
an induction motor type damping torque D .

## Slide 71: Swing Example
Here is a study involving a full dqo machine model with single
mass inertia and a single pole open and reclose feature at the relay
location R. There are two 100km distributed parameter lines
with a single phase fault half way along one of the lines.

## Slide 73: Multi-mass machine models
Single mass inertia models are probably OK for hydro turbine sets.
Steam turbines on the other hand have multiple stages (HP, IP, LP) plus the generator and exciter and may be much larger than the hydro sets.
Shafts have been damaged by mechanical resonances excited by sub-synchronous frequencies on the electrical network.

## Slide 74: Equations for the multi mass case
Each mass will now have a separate so that we now have a column vector for instead of a single variable.
The same is true for the other parameters in the equation of motion.
We have an additional term to take account of the different torques on each mass caused by the degree of twist on each of the input and output shafts.

## Slide 75: AVR’s, governors & PSS’s
In studies where the inertia of the set is relevant then we need to also include other devices which produce effects in the time window of interest.
Governors are in general very slow except in cases of “fast valving” on a steam set.
Automatic voltage regulators and Power Sytem Stabilisers will certainly be in play during power swing conditions.

## Slide 76: Features
The electrical models should allow for saliency (dqo) and saturation on the direct axis.
dqo models are useful for system studies.
For internal faults on machines phase domain (abc) models are required which preserve the identity of coil groups etc.

## Slide 77: Conclusions
Choose a model which suits the time scale of interest.
Where possible, compare any simulation results with recordings to check for model validity.
Models for internal faults are not generally available and are actively being researched at the present time.

## Slide 78: Transformer Models
By
Demetrios Tziouvaras
Schweitzer Engineering Labs, Inc.

## Slide 79: Transformer Models
Can be modeled in Emtp in three fundamental ways
  The Ideal transformer model
  The built-in saturable transformer model
  A model based on mutually coupled coils

## Slide 80: Ideal Transformer Model
Ideal Transformer
  Ignores leakage flux
    Assumes flux is confined in the core
  Neglects Magnetizing Currents
    Assumes no core reluctance

## Slide 81: Simple Transformer

## Slide 82: Ideal Transformer Equations

## Slide 83: Saturable Transformer Model
Uses a star-circuit representation
User could include saturation data
Good for single-phase transformers
Should not be used for 3-phase transformers

## Slide 84: Saturable Transformer Model
The model requires as a minimum the following data
  The voltage rating of each winding
  The leakage impedance of each winding
  The transformer connectivity information

## Slide 85: 3-Winding Transformer Model Parameters

## Slide 86: Saturable Transformer Model

## Slide 87: BCTRAN Admittance Matrix Model
This admittance matrix model represents a linear relationship between the primary and secondary voltages and currents
[R] and [wL]-1 must be separated

## Slide 88: BCTRAN Admittance Matrix Model
AUX routine generates 3-phase coupled R-L {Type 1,2,3,... punch file}
Two-port admittance matrix describing a non-ideal two winding transformer

## Slide 89: 3- Wdg Transformer
Data Required
  kV rating of each winding
  Winding connections
  Transformer ratings and impedances

## Slide 90: BCTRAN Model
Example
  3 - 1 Phase Transformers
  525/230/13.8 Auto
  200/267/334 Mva
  { Tertiary 33.6/44.8/56 Mva }
  Zhl = 7.30 % AT 200.0 MVA
  Zht = 7.04 % AT 44.8 MVA
  Zlt = 4.55 % AT 44.8 MVA

## Slide 91: BCTRAN Model
Example Continued
NO LOAD LOSS = 108.200 KW
% EXCITING CURRENT = 0.230 AT 100 % VOLTAGE
% EXCITING CURRENT = 0.820 AT 110 % VOLTAGE
H-L LOAD LOSS = 235.850 KW
H-T LOAD LOSS = 48.398 KW
L-T LOAD LOSS = 45.723 KW

## Slide 92: BCTRAN Model
$VINTAGE, 1
1GAT5A .2565000000E+00 .2055021807E+06
2GAT2A .0000000000E+00 .9001099424E+05
.8240000000E-01 .3943170426E+05
3GATTA GATTB .0000000000E+00 .9349570555E+04
.0000000000E+00 .4096002297E+04
.2300000000E-02 .4256690513E+03
1GAT5B .2565000000E+00 .2055021807E+06
2GAT2B .0000000000E+00 .9001099424E+05
.8240000000E-01 .3943170426E+05
3GATTB .0000000000E+00 .9349570555E+04
.0000000000E+00 .4096002297E+04
.2300000000E-02 .4256690513E+03
1GAT5C .2565000000E+00 .2055021807E+06
2GAT2C .0000000000E+00 .9001099424E+05
.8240000000E-01 .3943170426E+05
3 GATTA .0000000000E+00 .9349570555E+04
.0000000000E+00 .4096002297E+04
.2300000000E-02 .4256690513E+03
$VINTAGE, 0

## Slide 93: TRELEG Impedance Matrix Model
AUX routine generates mutually coupled R-L {Type 51,52,52,… punch file}
Exciting current must be nonzero
Matrices are read directly as coupled R-L branch data

## Slide 94: TRELEG Impedance Matrix Model
Short circuit reactance could be lost in wL
[wL] must be converted to actual quantities in very high precision {at least six significant digits}

## Slide 95: Transformer Saturation
Only when flux will exceed the linear region, about 1.05 p.u.
Academic otherwise

## Slide 96: Transformer Saturation
Must be considered in the following studies
  Transformer energization studies
  Load rejection studies
  Switching of transformer terminated lines
  Ferroresonance studies

## Slide 97: Eddy Currents
Eddy Currents have two Major Effects
  They Introduce Core Loses
  They Delay flux Penetration into the Core

## Slide 98: Eddy Currents
Difficult to model them correctly
No-load losses Include eddy current and hysteresis current losses
Could be represented with a resistance Rm in parallel with the magnetizing inductance

## Slide 99: High Frequency Equivalent
Emtp transformer models are valid for frequencies up to 2 kHz
To study phenomena with frequencies between 2 - 30 kHz, capacitive coupling among windings and ground must be added

## Slide 100: High Frequency Equivalent
Above 30 kHz a more detailed representation of internal winding arrangement is required
  Must model capacitances between windings and winding segments

## Slide 101: Transmission Line Models
By
Demetrios Tziouvaras
Schweitzer Engineering Labs, Inc.

## Slide 102: EMTP Transmission Line Models
Emtp users must know
  What kind of models are available
  Applicability of the various models for steady state or transient studies
  Advantages and disadvantages of each model

## Slide 103: EMTP Line Models for Steady State Studies
Line models for steady state studies
  Exact-pi model
  Nominal-pi model

## Slide 104: Exact-Pi Model
Exact-pi model
  It is a lumped-parameter model
  The model includes hyperbolic corrections
  Frequency independent
  Best model for steady state studies

## Slide 105: Exact-Pi Models
It is a multi-phase line model and it takes into account
  Skin effect and
  Ground return corrections
  Circuits in the same right-of-way
Not good for transient studies

## Slide 106: Nominal-Pi Model
Derived from the exact-pi model
  Ignores hyperbolic corrections
Takes into account
  Skin effect and
  Earth return corrections

## Slide 107: Nominal-Pi Model
Multi-phase line model
Frequency Independent
No time step limitations
Not good for transient Studies
  Could be used if multiple Nominal-pi sections are cascaded together

## Slide 108: Nominal-Pi Model
Model Limitations
  Cannot be Used for “Electrically Long Lines”
  Limited to lines with length < 150 Km at 60 Hz
  Limited to lines with length < 5 Km at 2 kHz

## Slide 109: EMTP Line Models for Transient Studies
Line models for transient studies
  Nominal-pi model
  Frequency independent distributed parameter line model
  Frequency dependent distributed parameter line model

## Slide 110: EMTP Line Models for Transient Studies
Nominal-pi
  Not recommended for transient studies
  Produces reflections at the cascading points
  Computationally expensive
  Sections must be kept very short { 5-10 km for frequencies up to about 2 kHz}

## Slide 111: EMTP Line Models for Transient Studies
Constant parameter distributed line model
  Model assumes that R’, L’, & C’ are constant
  L’ & C’ are distributed and the losses R’*l are lumped in three places
  Shunt losses are ignored

## Slide 112: EMTP Line Models for Transient Studies
The DP and FD models
  Use traveling wave solutions and are valid over a wider frequency range
  Require transformations between phase and modal domain
  Keep track of modal waves traveling at different speeds

## Slide 113: EMTP Line Models for Transient Studies
Drawbacks of transient models
  Approximations in the transformation matrix for untransposed lines
  Transformation matrix is taken as real and constant
  Less valid as asymmetry gets stronger

## Slide 114: EMTP Line Models for Transient Studies
Frequency dependent transmission line model
  Represents accurately the distributed nature of all line parameters
  Frequency Dependent
  Transformation matrix is real and constant
  Most accurate for use in transient studies

## Slide 115: EMTP Transmission Line Models
Transposition Issues
  Untransposed
  Balanced
  Double circuit line with zero sequence mutual coupling only
  Transposition averaging

## Slide 116: EMTP Transmission Line Models
Untransposed
  The transformation matrix
    It is a complex matrix
    It has different values at different frequencies
    For transient models it is taken as real valued and constant

## Slide 117: EMTP Transmission Line Models
Balanced
  The Line is assumed to be perfectly transposed
  All self and mutual Impedances and admittances are averaged
  Uses the Clarke transformation matrix
  Results could be less accurate unless the line is actually transposed

## Slide 118: EMTP Transmission Line Models
Double Circuit Model
  Applies to double circuit lines only
  Assumes that each three-phase circuit is perfectly balanced with respect to itself and the parallel three-phase circuit
  Assumes that coupling only exists in the zero sequence

## Slide 119: EMTP Transmission Line Models
Transposition Averaging
  Approximation to modeling each line transposition separately
  Model is based on averaging the series impedance and shunt admittance matrices
  Valid at low frequencies

## Slide 120: Conclusions
Use pi-exact model for steady state studies
Use fd-line models for lines of main interest in your study
Use cp-line models for lines of secondary interest

## Slide 121: Transmission Line Parameter Calculation
LINE CONSTANTS
    Auxiliary Routine
  LINE-PARAMETERS
    Its Output is the Series Impedance and Shunt Admittance Line Parameters
  LINE-MODEL
    Output is EMTP Line Models

## Slide 122: Transmission Line Parameter Calculation - Models
Models for Steady-State
  PI-EXACT
    Exact Single Frequency Pi-equivalent
Models for Transient Analysis
  FD-LINE
    Frequency Dependent Line Model
  CP-LINE
    Constant Parameter Line Model
  CORONA

## Slide 123: Transmission Line Parameter Data Structure
BEGIN NEW DATA CASE
LINE CONSTANTS
  Modules { CP-LINE, FD-LINE, ETC. }
  Units { ENGLISH, METRIC }
  Conductor Data
  BLANK
  Frequency Data
  Optional Control Cards { .NODES }
  BLANK Card Ending Frequency Data
  BLANK END OF DATA CASE

## Slide 124: Line Data
Voltage: 525 kV
Length: 112.7 miles
Tower: Single Circuit Flat Construction
Phase Conductor Data
  2156 MCM ACSR - Bluebird - 2/phase 18”
  Stranding: 19 Steel - 0.0961”
  84 Aluminum - 0.1602”
  Outside Diameter: 1.762” = D
  Core Diameter: 0.6408” = T

## Slide 125: Line Data
T/D = 0.363657
Rdc = 0.04495 Ohms/Mile at 500 C
Rac = 0.05050 Ohms/Mile at 500 C
2 Conductors/Phase Spaced at 18” Apart
32’ Phase-to-Phase Separation
Height at Tower = 98’
Height at Midspan = 45’
Circuit-to-Circuit Separation = 150’

## Slide 126: Line Data
Ground Conductor Data
  7#6 Allumoweld - 2 Conductors per Circuit Segmented
  Diameter: 0.486”
  Dc Resistance: 1.507 Ohms/Mile at 250C
  Height at Tower: 127’
  Height at Midspan: 98’
  Ground Conductor Separation: 58’

## Slide 127: Transmission Line Data
0 58’ 0
0 0 0 0 0 0
32’ 32’
98’
D
T

## Slide 128: Line Parameters
C ==============================================================================
BEGIN NEW DATA CASE
LINE CONSTANTS
C
C ----------------><Model --><Matrix -><Scale --><Fmin----><Npdec---><Ndec---->
LINE-PARAMETERS
C
C Unit->-------------------------------I
ENGLISH
C
C 500 kV lines 112.7 mi
C
C cSkin>Resis ->IX<React->Diam -->Hoiz -->Vtower->Vmid -->Separ ->Alpha>------NN
1.3637 0.04495 4 1.762 0.00 98.0 45.0 18.0 0.0 2
2.3637 0.04495 4 1.762 32.00 98.0 45.0 18.0 0.0 2
3.3637 0.04495 4 1.762 64.00 98.0 45.0 18.0 0.0 2
4.3637 0.04495 4 1.762 150.00 98.0 45.0 18.0 0.0 2
5.3637 0.04495 4 1.762 182.00 98.0 45.0 18.0 0.0 2
6.3637 0.04495 4 1.762 214.00 98.0 45.0 18.0 0.0 2
0 0.50 1.50700 4 0.486 6.00 127.0 72.0
0 0.50 1.50700 4 0.486 58.00 127.0 72.0
0 0.50 1.50700 4 0.486 156.00 127.0 72.0
0 0.50 1.50700 4 0.486 208.00 127.0 72.0

## Slide 129: Line Parameters
C
BLANK CARD - END OF CONDUCTOR CARDS
C
C Rho ->Fmatrx -->-----------<-IC->-<-IZ->-I<Along->-----I
100.0 60.0 000011 011000 1 112.7 1
C
BLANK
BLANK
C ==============================================================================
BEGIN NEW DATA CASE
BLANK CARD ENDS AUX ROUTINE

## Slide 130: Line Parameters: CP-LINE
C ==============================================================================
BEGIN NEW DATA CASE
LINE CONSTANTS
C
C ----------------><Model --><Matrix -><Scale --><Fmin----><Npdec---><Ndec---->
LINE-MODEL CP-LINE ZDOUBLE
C
C Unit->-------------------------------I
ENGLISH
C
C Midway - Vincent Double Circuit 112.7 mi
C
C cSkin>Resis ->IX<React->Diam -->Hoiz -->Vtower->Vmid -->Separ ->Alpha>------NN
1.3637 0.04495 4 1.762 0.00 98.0 45.0 18.0 0.0 2
2.3637 0.04495 4 1.762 32.00 98.0 45.0 18.0 0.0 2
3.3637 0.04495 4 1.762 64.00 98.0 45.0 18.0 0.0 2
4.3637 0.04495 4 1.762 150.00 98.0 45.0 18.0 0.0 2
5.3637 0.04495 4 1.762 182.00 98.0 45.0 18.0 0.0 2
6.3637 0.04495 4 1.762 214.00 98.0 45.0 18.0 0.0 2
0 0.50 1.50700 4 0.486 6.00 127.0 72.0
0 0.50 1.50700 4 0.486 58.00 127.0 72.0
0 0.50 1.50700 4 0.486 156.00 127.0 72.0
0 0.50 1.50700 4 0.486 208.00 127.0 72.0

## Slide 131: Line Parameters: CP-LINE
C
BLANK CARD - END OF CONDUCTOR CARDS
C
C Rho ->Fmatrx -->--------------------------Along ->-----I
100.0 60.0 112.7 1
C
C ----------------><k-a >< ><m-a >< ><k-b >< ><m-b >< ><k-c >< ><m-c >
.NODES MV52SA VM52NA MV52SB VM52NB MV52SC VM52NC
MV51SC VM51NC MV51SB VM51NB MV51SA VM51NA
C
BLANK
BLANK
C ==============================================================================
BEGIN NEW DATA CASE
BLANK CARD ENDS AUX ROUTINE

## Slide 132: Line Parameters - Output
---> Z IMPEDANCE MATRIX (OHM/MILE)
+ E FOR THE SYSTEM OF EQUIVALENT PHASE CONDUCTORS
ROWS AND COLUMNS PROCEED IN SAME ORDER AS SORTED INPUT
1 1.15631E-01
1.11387E+00
2 9.09384E-02 1.15635E-01
5.46915E-01 1.11384E+00
3 9.08819E-02 9.09388E-02 1.15632E-01
4.62832E-01 5.46912E-01 1.11386E+00
4 9.06024E-02 9.07339E-02 9.08381E-02 1.15632E-01
3.59528E-01 3.88590E-01 4.26923E-01 1.11386E+00
5 9.04447E-02 9.06025E-02 9.07339E-02 9.09388E-02 1.15635E-01
3.36123E-01 3.59528E-01 3.88590E-01 5.46912E-01 1.11384E+00
6 9.02620E-02 9.04447E-02 9.06024E-02 9.08819E-02 9.09384E-02 1.15631E-01
3.16537E-01 3.36123E-01 3.59528E-01 4.62832E-01 5.46915E-01 1.11387E+00

## Slide 133: Line Parameters - Output
---> Z IMPEDANCE MATRIX (OHM/MILE)
+ S FOR THE SYMMETRICAL COMPONENTS OF THE EQUIVALENT PHASE CONDUCTORS
ROWS PROCEED IN SEQUENCE 0,1,2, 0,1,2 ETC. AND COLUMNS PROCEED IN SEQUENCE 0,2,1, 0,2,1 ETC.
0 2.97472E-01
2.15163E+00
1 -2.42756E-02 -4.85348E-02
-1.39891E-02 2.80639E-02
2 2.42549E-02 2.47132E-02 4.85713E-02
-1.40236E-02 5.94972E-01 2.80006E-02
0 2.71755E-01 2.59890E-02 -2.64347E-02 2.97472E-01
1.09049E+00 -3.92647E-02 -3.90376E-02 2.15163E+00
1 -2.05902E-02 5.42438E-03 -1.54766E-03 -2.42722E-02 -4.85349E-02
4.24119E-02 -3.10158E-03 -5.95370E-03 -1.39935E-02 2.80637E-02
2 2.10097E-02 1.60009E-03 -5.39823E-03 2.42527E-02 2.47132E-02 4.85715E-02
4.21394E-02 -5.95237E-03 -3.14686E-03 -1.40287E-02 5.94972E-01 2.80005E-02

## Slide 134: Line Parameters - Output
##### SYMMETRICAL COMPONENTS WAVE QUANTITIES #####
SEQUENCE SURGE IMPEDANCE ATTENUATION VELOCITY WAVELENGTH RESISTANCE REACTANCE SUSCEPTANCE
MAGNITUDE(OHM) ANGLE(DEGR.) DB/MILE MILES/SEC MILES OHM/MILE OHM/MILE S/MILE
ZERO 6.80545E+02 -3.93574E+00 1.90283E-03 1.18395E+05 1.97325E+03 2.97472E-01 2.15163E+00 4.68992E-06
POSITIVE 2.86842E+02 -1.18925E+00 3.74252E-04 1.81634E+05 3.02723E+03 2.47132E-02 5.94972E-01 7.23746E-06

## Slide 135: Distributed Parameter Line Model
C BALANCED-LINE MODELLING. PARAMETERS AT F = 6.0000E+01 HZ
$VINTAGE,1
C R' IN OHMS/KM, ZC IN OHMS, TAU IN SEC, LENGTH IN KM
-1MV53SAVM53NA 1.85504E-01 6.57236E+02 8.67548E-04 1.65762E+02 2 00
-2MV53SBVM53NB 1.57442E-02 3.02964E+02 5.68033E-04 1.65762E+02 2 00
-3MV53SCVM53NC
$VINTAGE,0

## Slide 136: Distributed Parameter Line Model
C ZERO-SEQ-COUPLED MODELLING. PARAMETERS AT F = 6.0000E+01 HZ
$VINTAGE,1
C R' IN OHMS/KM, ZC IN OHMS, TAU IN SEC, LENGTH IN KM
-1MV52SAVM52NA 3.53701E-01 8.56557E+02 1.13153E-03-1.81373E+02 2 06
-2MV52SBVM52NB 1.59801E-02 4.62503E+02 6.85883E-04-1.81373E+02 2 06
-3MV52SCVM52NC 1.53560E-02 2.86721E+02 6.20338E-04-1.81373E+02 2 06
-4MV51SCVM51NC 1.53560E-02 2.86721E+02 6.20338E-04-1.81373E+02 2 06
-5MV51SBVM51NB 1.53560E-02 2.86721E+02 6.20338E-04-1.81373E+02 2 06
-6MV51SAVM51NA 1.53560E-02 2.86721E+02 6.20338E-04-1.81373E+02 2 06
$VINTAGE,0
.40824829 .40824829 .70710678 .40824829 .00000000 .00000000
.00000000 .00000000 .00000000 .00000000 .00000000 .00000000
.40824829 .40824829 -.70710678 .40824829 .00000000 .00000000
.00000000 .00000000 .00000000 .00000000 .00000000 .00000000
.40824829 .40824829 .00000000 -.81649658 .00000000 .00000000
.00000000 .00000000 .00000000 .00000000 .00000000 .00000000
.40824829 -.40824829 .00000000 .00000000 .70710678 .40824829
.00000000 .00000000 .00000000 .00000000 .00000000 .00000000
.40824829 -.40824829 .00000000 .00000000 -.70710678 .40824829
.00000000 .00000000 .00000000 .00000000 .00000000 .00000000
.40824829 -.40824829 .00000000 .00000000 .00000000 -.81649658
.00000000 .00000000 .00000000 .00000000 .00000000 .00000000

## Slide 137
Section 9.0
NONLINEAR ELEMENTS

## Slide 138
Fundamentals of nonlinear element modeling :
1. Transformers
2. Lightning arresters
3. Current-limiting fuses

## Slide 139
Transformers

## Slide 140
Transformer Model
n:1
Ideal
Transformer
Ls
Rp
Lp
Lm
Rs

## Slide 141
Voltage
Current
Operating point
for current transformers
Linear region
Non-Linear region
V-I curve knee point
Transformer V-I Curve Characteristic
More in Section 10
Saturation voltage
Operating point
for voltage transformers

## Slide 142
Lightning Arresters

## Slide 143
Voltage
Current
Lightning Arrester V-I Curve Characteristic
÷
÷
ø
ö
ç
ç
è
æ
v
v
p
=
i
ref
q

## Slide 144
0
5
10
15
20
25
30
0
50
100
150
200
250
p1=173780
p1=40000
p1=80000
p1=120000
Voltage [kV]
Current [kA]
÷
÷
ø
ö
ç
ç
è
æ
v
v
p
=
i
ref
q
q1=1/30

## Slide 145
Fuses

## Slide 146
EXPULSION FUSES
CURRENT-LIMITING FUSES

## Slide 147
EXPULSION FUSES await current passing
through zero to extinguish the contained
arc and clear the circuit
All expulsion fuses require at least
one-half cycle
before they can clear the fault

## Slide 148
-20
-15
-10
-5
0
5
10
15
0
5
10
15
20
25
30
35
40
45
Time [ms]
Current [kA]
(multiplier 0.1x)
Voltage [kV]

## Slide 149
CURRENT-LIMITING FUSES typically have a
silver ribbon element surrounded by fine
granular silica sand housed in an insulating tube
Typically, current-limiting fuses can interrupt
currents up to 50,000 A and, in the process,
limit peak current magnitude and
reduce fault time duration

## Slide 150
Melting
Arcing
0
0.005
0.01
0.015
0.02
0.025
-2000
-1000
0
1000
2000
3000
4000
5000
Asymmetrical
Available Current [A]
CLF
Let-thru Current
Time [s]

## Slide 151
0
0.01
0.02
-20
-10
0
10
20
Voltage [kV]
Current [kA]
(multiplier 0.1x)
Time [s]
8.3 kV, 20 A CLF Fuse Current and Voltage

## Slide 152
Simulations

## Slide 153
0
1
2
3
4
5
6
7
0.01
0.1
1
10
100
Time [ms]
Resistance [W]
8.3 kV, 65 A CLF Fuse
Voltage peak

## Slide 154
The main two parameters in the CLF operation
for model development:
1. fuse's melt I2t
2. fuse's non-linear resistance characteristic
after melting open.
The melt I2t is independent of either
1. available fault current or
2. fault incidence angle

## Slide 155
0
0.01
0.02
0.03
-15
-10
-5
0
5
10
15
20
25
1
3
4
2
Comparison of Tested and Simulated
CLF Voltages and Currents
1 - Tested Voltage [kV]
2 - Tested Current [kA]
3 - Simulated Voltage [kV]
4 - Simulated Current [kA]
Time [s]

## Slide 156
Nonlinear Models
Pseudononlinear Models
True nonlinear Models

## Slide 157
Pseudononlinear Models
The nonlinearity is defined as
piece-wise linear characteristics
(as in the case of transformer V-I curves)

## Slide 158
L
V
R
I
L
V
L
A Circuit Containing Non-Linear Inductor

## Slide 159

i
L
(
t
)
(
t -
t)
iL(t-  t)
slope
kn
Non-linear Element Represented as
Piece-Wise Linear -i Function
iL(t)

## Slide 161
(
)
(
)
)
(
)
(
)
(
)
(
i
t
t
k
v
t
i
t
t
t
k
v
t
t
G
t
k
h
t
t
i
t
t
t
k
v
t
t
L
n
L
L
n
L
L
n
L
n
L
=
+
-
+
-
=
-
=
-
+
-
D
D
D
D
D
D
D
D
D
2
2
2
2
(
)

## Slide 163
    The Circuit with its Discrete Time Equivalent
G
L
-1
h(t-
dt
)
V
Vl
R
i
L
(history)

## Slide 164
The Pseudononlinear Elements
Type-98 Reactor
Type-96 Hysteretic Reactor
Type-97 Staircase Time-Varying Resistance
Type-99 Resistance

## Slide 165
Type 98
Pseudononlinear Reactor
 = (i)
Can be used for transformer non-linear
magnetizing branch modeling

## Slide 166
Type 96
Pseudononlinear Hysteretic Reactor
 = (i)
Very similar to Type 98
Can represent the
hysteretic behavior of the core material

## Slide 167
        Type 97
        Staircase Time-Varying Resistance
        Can represent a time-varying resistance
        R = f(t)
        which changes in a staircase manner
        Can be used to model
        current-limiting fuses

## Slide 168
Type 99
Pseudononlinear Resistance
Input data specified as a piece-wise
linear characteristic
V = f(i)
Can model gapped or gapless lightning arresters

## Slide 169
        True nonlinear models
The nonlinearity defined as a non-linear function
e.g. flux  as a function of the current I
 =(i)
Uses a Newton-Raphson iterative solution
Type-91 Time-Varying Resistance
Type-92 Piece-Wise Linear Resistance
Type-93 Piece-Wise Linear Reactance

## Slide 170
        Type 91
        Specified as a piece-wise linear characteristic
        R=f(t)
        Linear interpolation between points
        Can be used to model
        current-limiting fuses

## Slide 171
        Type 92
        Specified as a piece-wise linear characteristic
        V = f(i)
        Linear interpolation between points
        Can be used for modeling
        gapped or gapless lightning arresters

## Slide 172
        Type 93
        Specified as a piece-wise linear characteristic
         = f(i)
        (  is the total flux linkage )
        Linear interpolation between points
        Can be used to model
        transformer magnetizing branch

## Slide 173
  Support Routines
  for  - i curve generation
Converts the Vrms- Irms characteristics
into peak- ipeak

## Slide 174
  Support Routines
  for HYSTERESIS generation
Type 96 element can represent
hysteresis and remanence in the core
Generates hysteresis loop
from the known flux-current curve
It takes one point and generates curve for
one magnetic material

## Slide 175
3. CT Model using Type 96 Element
Current
Flux

## Slide 176
Current
Flux
0
0

## Slide 177
Lightning Arrester Model

## Slide 178
C Intermediate Arrester AZF27kV
C
92BUS01AGRND0A 4444.
C RLIN | VFLASH | VZERO
.0 -1.
C CURRENT | VOLT |
1. 43269.
10. 45810.
100. 49078.
500. 53579.
1000. 55829.
2000. 58588.
20000. 66000.
9999.
Voltage
Current
Model_File

## Slide 179
C 27kV VariGAP
92BUS01A 4444.
C RLIN | VFLASH | VZERO
.0 63640.
C CURRENT | VOLT |
1. 35760.
10. 37860.
100. 40560.
500. 44280.
****** ********
****** ********
6000. 55000.
8000. 60000.
20000. 65000.
9999.

## Slide 180
Current-Limiting Fuse Model

## Slide 181
C **********************************
C 8.3 kV, 65 A ELF FUSE
91CLF65A 3333. 3
0.001
$INCLUDE C:\PAPERS\MEA96\CLF65A\E65a8v.mod
9999.
C *****************
E65a8v.mod
1.2187772e-002 2.0000000e-005
1.3187587e-002 4.0000000e-005
1.4340653e-002 6.0000000e-005
1.5443534e-002 8.0000000e-005
1.6447810e-002 1.0000000e-004
Model_File
Time
Resistance

## Slide 182
Type 94
nonlinear component modeling
using MODELS
Thevenin Type 94
Iterated Type 94
Norton Type 94

## Slide 183
Type 94 is a nonlinear single or
multi-phase circuit component
It can simulate arbitrary nonlinear
element or circuit
The operation of the component is
described in MODELS, or in other
languages called from MODELS

## Slide 184
Thevenin Type 94
the component sees the
rest of the linear circuit as a
Thevenin equivalent, and
calculates the
current at each time step
(good for one component)

## Slide 185
Iterated Type 94
a group of nonlinear components
see the rest of the linear circuit as a
Thevenin equivalent, and each calculate
their current corresponding to
estimated voltages provided by ATP's
Newton iteration algorithm
(good for more than one components)
Both approaches provide a solution
synchronized with the rest of the circuit

## Slide 186
Norton Type 94
component is a Norton equivalent
(an admittance to ground in parallel with a
current source). For a multi-phase component,
the admittance to ground is a matrix, and
there is a current source at each node
At each time step, the component receives
node voltage values, and calculates the
admittance and current source to be used at
the next time step
No iteration is performed by ATP

## Slide 187
Changes in values take effect with
one time step delay
The time step delay is not a problem for
passive components, as this is the same
method already used in ATP for
representation of
inductances, capacitances, and
transmission lines

## Slide 188
Type-94 format
94A1 B1 M1 ITER
94A2 B2
94A3 B3
>DATA D1 xxxxxxxxxx
>DATA D2 xxxxxxxxxx
>SSV KA { Voltage(t=0) at left-node #1 KA
>SSV { " " " #2 = default existing value at A2
>SSV KB { " " " " #3 = voltage at node KB
>SSV KC { Voltage(t=0) at right-node #1 KC
>SSV { " " " #2 = default existing value at B2
>SSV KD { " " " " #3 = voltage at node KD
>SSI KA { Current(t=0) into left-node #1 KA
>SSI { " " " " " #2 = default value of zero
>SSI KB { " " " " #3 = current in switch KB
>END
Type 94

## Slide 189
Section 10
Relay Input Sources

## Slide 190
np
CT load
(burden)
ns
ip
is

## Slide 191
Burden
Magnetizing
Branch
ip
Rp
Lp
Ls
Rs
is
Ideal
CT

## Slide 192
ip’
Rp
Lp
Ls
Rs
is
Es
im
imr
imx
Lm
Rm
Rl

## Slide 193
ip’
is
Es
im
Lm
Rb
Current
source

## Slide 194
Short Circuit Currents

## Slide 195
Simulations
-1
0
1
2
Time
Current

## Slide 196
0
20
40
-1
0
1
2
Time [ms]
Current

## Slide 197
0
0.01
0.02
0.03
0.04
0.05
Time [s]
Current [A]
Symmetric
Asymmetric
-150
-100
-50
50
100
150
200
0

## Slide 198
0
0.02
0.04
0.06
0.08
0.1
0
20
40
60
80
100
Time [s]
Current [A]
Symmetric
Asymmetric

## Slide 199
10
100
1000
CT ratio
error [%]
600/5 A, C100 CT
with 1.5 W total load resistance
Ideal CT
10
100
1000
CT Primary Current [A] (referred to the secondary)
CT Secondary Current [A]
CT Saturation for Symmetric Fault Currents
0.1
1
10
100
10
100
Exciting Current [A]
Voltage [V]
15
23
35
48
7

## Slide 200
Lm is nonlinear inductor,
specified in piecewise linear form
-I data points are not readily available
ATP provides a routine SATURATION to
convert Vrms-Irms characteristics
into -I set

## Slide 201
Flux
Current
Flux-Current Characteristic
Representing the Noise

## Slide 202
Example:
Modeling a
600/5 A Current Transformer

## Slide 203
        This example includes 5 files:
1. Flux-Current curve generation
2. CT model using Type 98 element
3. Hysteresis generation
4. CT model using Type 96 element
5. Simulation of the CT V-I curve
measurement (verifies proper modeling)

## Slide 204
    1. Input File for Flux-Current Curve Calculation
    (Type 98 model based on the V-I p.u. values)
BEGIN NEW DATA CASE
SATURATION
60. 5.e-3 25.0e-6 1
1.0722322e-3 4.1719300e-1
1.9397460e-3 9.8089860e-1
.
.
.
2.4254340 2.7519700e+1
9999.
BLANK CARD ENDING PLOTS
BEGIN NEW DATA CASE
BLANK CARD ENDING CASE
Current
Voltage
V-I p.u. values

## Slide 205
2. CT Model using Type 98 Element
TRANSFORMER CTA1
9999.
C TRANSFORMER WINDINGS
01CTIN1A 1.E-7 1.E-9 5.
02 SEC21A 1.E-4 1.E-6 600.
98SEC21A .01279.0184
0.0075818266 0.0078251180
0.0127888317 0.0183983128
0.0258246561 0.0471187672
.
.
.
27.6428084758 0.5161757276
9999.
SEC21ACTOUTA .22 1.
Simulations

## Slide 206
    4. Input File for the Hysteresis
    Curve Generation
BEGIN NEW DATA CASE
HYSTERESIS
C 88.
1 4 1
5283.45 77.57983
BLANK CARD ENDING PLOTS
BLANK EGIN NEW DATA CASE
BLANK CARD ENDING CASE

## Slide 207
3. CT Model using Type 96 Element
TRANSFORMER CTA1
9999.
C TRANSFORMER WINDINGS
01CTIN1A 1.E-7 1.E-9 5.
02 SEC21A 1.E-4 1.E-6 600.
96SEC21A 8888.
-1.98129375E+03 -7.57544222E+01
-1.32086250E+03 -7.52980703E+01
.
.
.
7.26474375E+03 7.80361819E+01
9999.
SEC21ACTOUTA .22 1.

## Slide 208
R
A1
A2
CT model
primary
secondary
open
V-I Curve Measurement Simulation

## Slide 209
    5. Input File for V-I Curve Measurement Simulation
    (one V-I point shown )
BEGIN NEW DATA CASE
.1E-3 .034 0. 0.
1000 1 1 1
C
LINE2ACTOUTA .001 1
C
C TRANSFORMER Model
$INCLUDE c:\papers\ct_ieee\vi\ct600.mod
C
BLANK
LINE1ALINE2A -1. .3
BLANK CARD ENDING SWITCH
14LINE1A 120. 60. 0. -1.
BLANK CARD ENDING SOURCE
CTOUTA
BLANK CARD ENDING NODE VOLTAGE OUTPUT
BLANK

## Slide 210
0.001
0.1
1
10
100
1
10
100
1000
Exciting Current [A]
Voltage [V]
    A 600/5 A CT V-I Characteristic
    (measured and simulated)

## Slide 211
9.2
Digital Models of
Coupling Capacitor Voltage Transformers
CCVT

## Slide 212
A CCVT Circuit Connection

## Slide 213
HV
C
C
1
2
L
R
G
G
C
R
R
L
L
R
G
R
C
L
R
C
L
y
y
R
y
Z
1
2
d1
d1
d1
1
2
ps
p
r
2
s
3
b
h
T
F
F
F
3
a
a
Cp
d1
C
C
p
p
R
C
L
C
s
s
x
x
x
R
1
3
138kV
5kV/115V/66.4V
SW1
A 138 kV CCVT Design

## Slide 214
2
1
C
C
HV
C
C
C
p
p
p
m
m
C
C
R
L
R
L
L
R
b
R
FSC
Generic CCVT Model

## Slide 215
10
1
10
2
10
3
10
4
Frequency [Hz]
Cc
higher
Cp
higher
Cp
smaller
Ce
higher smaller
Cc
smaller
Gain [db]
Cc & Cp
neglected
    CCVT Frequency Response
2
1
C
C
HV
C
C
C
p
p
p
m
m
C
C
R
L
R
L
L
R
b
R
FSC

## Slide 216
a) b) c)
    A) FSC Circuit Diagram
    B) FSC Digital Model (Lf represented as inductor)
    C) FSC Digital Model (Lf represented as transformer)
Cf
Lf
Rf
Cf
Lf
Rf
Cf
Lf
Rf

## Slide 217
0
100
200
300
400
500
600
700
FSC Impedance [W]
10
100
1000
Frequency [Hz]
A
Cf
Lf
Rf
    FSC Circuit Diagram

## Slide 218
0
100
200
300
400
500
600
700
FSC Impedance [W]
10
100
1000
Frequency [Hz]
A
B
Cf
Lf
Rf
FSC Digital Model
(Lf represented as inductor)

## Slide 219
0
100
200
300
400
500
600
700
FSC Impedance [W]
10
100
1000
Frequency [Hz]
A
C
Cf
Lf
Rf
FSC Digital Model
(Lf represented as transformer)

## Slide 221
10
100
1000
10000
-80
-60
-40
-20
0
20
Gain [db]
Frequency [Hz]
ATP
Simulation
Measurement
    PCA-5 CCVT Frequency Response
    (Measured vs. ATP Simulation)

## Slide 222
2
1
C
C
HV
C
C
C
p
p
p
m
m
C
C
R
L
R
L
L
R
b
R
FSC

## Slide 223
CCVT Modeling
using
Transfer Function and Fitting Method

## Slide 224
    Single-Line-to-Ground Fault
    (recorded at the CCVT secondary and Haefely divider)

## Slide 225
Time Response of the 500 kV TEHM CCVT

## Slide 226
10
0
10
1
10
2
10
3
10
4
-50
-40
-30
-20
-10
0
10
Frequency [Hz]
Gain [db]
  Frequency Response of the 500 kV TEHM CCVT
  obtained from Measurements and
  calculated using MATLAB

## Slide 227
500 kV / 3
C1
C2
Cc
Lc, Rc
Cp
SDT
Load
Rp
Lp
Rs
Ls
115 V
500 kV TEHM CCVT Circuit Connection
adopted for ATP Modeling

## Slide 228
Table 2. Estimated The 500 kV CCVT Parameters
C1
C2
Rc
Lc
Cc
SDT ratio
Rp
Lp
Cp
Rs
Ls
Load (assumed)
5210 pF
123050 pF
500
W
50.7 H
600 pF
11.73 kV/115 V
296
W
6.5 H
600 pF
1 mW
1 mH
100
W

## Slide 229
10
100
1000
10000
-50
-40
-30
-20
-10
0
10
Frequency [Hz]
20*log(vs/vp)
    ATP Simulations of 500 kV TEHM CCVT
    Frequency Response (frequency scan)

## Slide 230
Voltage Transformer
Digital Models

## Slide 231
n:1
Ideal
Transformer
Ls
Rp
Lp
Cp
Rm
Lm
Rs

## Slide 232: Additional Modeling Considerations
By
Demetrios Tziouvaras
Schweitzer Engineering Labs, Inc.

## Slide 233: Switch Modeling
Ordinary switches
  Time controlled switch
    Conventional deterministic switch
  Voltage controlled switch
  Statistics switch
    Random closing/opening switch
  Systematic switch

## Slide 234: Time Controlled Switch
Model circuit breakers
Model short circuits
Other similar switching devices
Modeled as ideal
  I = 0 when open ( R=infinity)
  DV=0 when closed ( R=0)

## Slide 235: Simple Breaker Model

## Slide 236: Voltage Controlled Switch
Simulate protective gaps
Surge arrester gaps
Series capacitor gaps
Flashovers across insulators

## Slide 237: Voltage Controlled Switch
Normally open at the start of the simulation
Closes when the voltage across the switch exceeds a user-defined flashover value
Opening occurs at the first current zero, provided the user defined delay time has elapsed

## Slide 238: Voltage Controlled Switch

## Slide 239: Measuring Switch
Switch is always closed
  During steady state
  During transient simulation
It is used to obtain current, power or energy in places where these quantities are not otherwise available

## Slide 240: TACS Switches
TACS - Controlled switches
  Type 11 - Simulates diodes where current flows in one direction
  Type 12 - can be used to simulate triacs and spark gaps
  Type 13 - General TACS controlled switch

## Slide 241: Load Models
Load models should satisfy two requirements
  The power frequency MVA load should be accurate in order to set up the proper initial conditions
  The low and high frequency characteristics should also match the physical load to properly represent its effects on harmonics and transients

## Slide 242: Series and Parallel RL Load Models
Series RL and Parallel RL models
  Produce correct initial conditions
  Inaccurate at higher frequencies
    Series RL provides very little damping at high frequencies
    Parallel RL provides a constant damping at higher frequencies

## Slide 243: Load Models
Improved load model
  Combination of a series RL with a parallel RL model
  10 % of load dissipated on the series RL circuit - represents distribution transformers
  90 % of load dissipated on the parallel RL circuit - customer load

## Slide 244: Transient Analysis of Control Systems
By
Demetrios Tziouvaras
Schweitzer Engineering Labs, Inc.

## Slide 245: Transient Analysis of Control Systems
TACS
  TACS was designed for the simulation of control systems
  Initially it was designed for the Pacific Intertie HVDC converter controls

## Slide 246: Applications of TACS
TACS can be used to simulate
  Synchronous machine excitation controls
  Response of static or digital relays
  Series capacitor protection controls
  HVDC converter controls, etc.

## Slide 247: TACS Interface with Emtp
TACS is solved separately from the network
  There is one time step delay between TACS and emtp solution
  Emtp output is used as TACS input over the same time step
  TACS output becomes emtp input the next time step

## Slide 248: Interface Between TACS and Emtp

## Slide 249: Interaction Between Control System and Power System
“Sensors” in the network pick up node voltages and switch currents
Variables from TACS are forwarded to the network
  Network elements must be set to receive commands from TACS, i.e.., TACS controlled switches

## Slide 250: Transient Analysis of Control Systems
TACS consists mainly of:
  Transfer function blocks
  Signal sources
  Special devices
  FORTRAN statements

## Slide 251: Models Available in TACS
Transfer Functions
  Basic building blocks defined by the Laplacian s-operator
  The program converts the s-domain functions to algebraic difference equations
  Static and dynamic limiters available

## Slide 252: Typical Excitation Control System of a Generator

## Slide 253: Models Available in TACS
TACS sources
  They are time dependent sources
  DC source
  Ramp
  Step
  Pulse, Sinusoidal, etc.

## Slide 254: Models Available in TACS
Devices are control system subsystems that are used frequently, for example
  Frequency sensor
  Digitizer
  Controlled integrator
  Sample and Track, etc.

## Slide 255: Models Available in TACS
FORTRAN Expressions
  Algebraic
  Relational
  Logical
Some restrictions apply
  Cannot implement all of FORTRAN

## Slide 256: FORTRAN Restrictions
Cannot define arrays
DO and GOTO statements are not allowed
Intrinsic functions accept one argument only
  Above restrictions severely limit the flexibility of FORTRAN

## Slide 257: Initialization of TACS Variables
Initial conditions of the electrical network are calculated before TACS
  All TACS defined variables are still zero
  TACS variables must be initialized in order to get a meaningful steady state electrical network solution

## Slide 258: Example of a Machine Excitation System

## Slide 259: Machine Excitation System

## Slide 260: Tacs Excitation Model

## Slide 261: Initial Conditions

## Slide 262: Conclusions
TACS is very powerful tool
Must be careful with time step delays introduced by TACS
Must be careful with initial conditions

## Slide 263: EMTP Tutorial
Relay Models for use in EMTP

## Slide 264: Outline
Introduction
  Modeling approaches
  Components of a model
  Previous Activities - Modeling
Transducer Models
Signal Conditioning Filters
Analog to Digital Conversion
Computing Phasors
Modeling Relay Dynamics

## Slide 265: Introduction
Modeling approaches
  Phasor-based models
  Transient models
    Attached with emtp - using TACS …
    Models outside the emtp
      FORTRAN
      MATLAB
      APL
      C++

## Slide 266: Introduction
Components of a model
  Dictated by the objective of the study
    For transient studies - Models must represent the transient and relay performance faithfully
  Components?

## Slide 267: Major Components

## Slide 268: Historical perspective
Early studies [213]
  Fortran and later in APL
  Computed phasors and calculated frequency
  Calculated impedance
  Determined direction of power flow
  Applied logic to model relay operation

## Slide 269: Relays modeled
Overcurrent relays
Directional relays
Distance relays

## Slide 270: Processes Modeled
Finite length of A/D converters
Word size of processors
Assumptions made in the algorithms
Approximations made in implementations

## Slide 271: Algorithms Modeled
Fourier transform
Least squares fit
Kalman filters

## Slide 272: Special Models
Assembly language model [214-216]
  Modeled
    processor
    software instructions
    finite length of A/D converters, word size of the processor, moving data between memory and registers and algorithms including assumptions
    Determined glitches, errors, timing problems, completion of computations (one sampling interval or not)

## Slide 273: Another special model
Automated model development [217]
  Models algorithms and
  components that affect the performance of the algorithm
    Antialiasing filters
    A/D converters
  Has two software modules
    Collect interactively relay specifications
    Produce MATLAB code of the model

## Slide 274: Transducer Models
Voltages and currents
  Power system level
    4 - 800 kV and 50 - 50,000 A
  Relay level
    120 V and 5A
    these are suitable for electromechanical relays
  Reduced to 5 - 10 V peak value for use in solid-state and numerical relays using auxiliary vts and cts

## Slide 275: Transducer Models
Most transient programs include
  ct and vt models
    models of magnetic cores of cts
    models of magnetic cores of inductors used with cvts
  Models of auxiliary transformers must be included

## Slide 276: Signal Conditioning
Power system voltages and currents include
  harmonics
    Magnetic cores, Rectifiers and inverters and Speed control devices
  other high frequency components
    Traveling waves, Arc furnaces and Power electronic control devices

## Slide 277: Signal Conditioning
Electromechanical relays
  inherently immune to the presence of high frequency components
Sold-state state and numerical relays
  high frequency components are removed by signal conditioning filters

## Slide 278: Signal Conditioning
Consists of
  Reduction of signal level
  Remove high frequency components using lowpass filters
  protect from transients
    isolate from power system
    clip signal when too strong

## Slide 279: Signal conditioning filters
Must model filters
  because they change the composition of signals substantially

## Slide 280: Signal Conditioning
  Transfer function of a fourth order filter could be
  For cutoff frequency of 300 Hz and data rate of 11,520 Hz, transfer function is

## Slide 281: Signal Conditioning
  Digital filter by bilinear transformation
  replace
  Adjust for warping

## Slide 282: Signal Conditioning
The algorithm to implement this filter in a numerical model that works out to
This is a recursive equation; the analog filter is not.

## Slide 283: Analog to Digital Conversion
Numerical relays use A/D converters
A/D conversion is a two step process - sampling and quantizing
Sampler is assumed to be a perfect device

## Slide 284: Analog to Digital Conversion
The output of an A/D converter is a word of 8, 12, 16, 24 or 32 bits.
MSB LSB

## Slide 285: Quantization errors - rounding
  Let us define error as
En = sq(n) - s(n)
Range of errors
-0.5 LSB < En < +0.5 LSB
saturation

## Slide 286: Quantization
  For an instantaneous value in the range of
-VAD < v < +VAD
  and two’s complementary arithmetic, quantized values are
  negative numbers:
  positive numbers:

## Slide 287: Computing Phasors
Digital filters extract components of selected frequencies
Quadrature components combined to obtain phasors

## Slide 288: Computing Phasors
Several techniques are available such as
  Discrete Fourier Transform
  Least squares curve fitting
  Kalman filters
  Wavelet transform
For modeling a relay, it is essential that type of algorithm used by the relay should be known.

## Slide 289: Relay Dynamics
Inverse Time Overcurrent Relay
Admittance Relay
Quadrilateral Relay

## Slide 290: Inverse Time O/C Relay
Current-Time characteristic

## Slide 291: Inverse Time Overcurrent Relay
  Any of these characteristics can be expressed in the form of
  Implement time delay by

## Slide 292: Inverse Time Overcurrent Relay
  Numerical model of an inverse time overcurrent relay
  for I  Pickup value
  for I > Pickup value

## Slide 293: Admittance Relay
Electromechanical
Solid-state
Digital (Numerical)

## Slide 294: Electromechanical and Solid-State Relays
Amplitude comparator
Phase comparator

## Slide 295: EM & Solid-State Relays
Issues
  Phase shifting
  Induction motor (EM)
  Phase difference measurements

## Slide 296: Phase Shifting
Use RL circuit to obtain IZR EM relays

## Slide 297: Phase Shifting
Phase shifting in solid-state relays

## Slide 298: Phase Comparator

## Slide 299: Numerical Mho Relay

## Slide 300: Numerical Quadrilateral Relay

## Slide 301: Conclusions
Relay models in emtp - TACS
Relay models attached to emtp -
Models should represent the relay hardware (and software) adequately
Models of some components will never be perfect
Models should be used to identify critical cases